## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: April 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 17382.86 |  | 415549 |  | 35.9253 |  | 31774 |  | 2662361 |  | 13975.34 |  |  |  |  | 4514.89
1 | 17389.41 | 6.55 | 476146 | 0.060597 | 35.9254 | 0.0001 | 31869 | 0.095 | 2754999 | 0.092638 | 13981.21 | 5.87 | 733.93 | 26684 | 538.07 | 4514.89 | 0
2 | 17394.92 | 5.51 | 667241 | 0.19109 | 35.9827 | 0.0573 | 32012 | 0.143 | 2842467 | 0.087468 | 13986.45 | 5.24 | 733.92 | 26669 | 538.02 | 4514.89 | 0
3 | 17398.94 | 4.02 | 823193 | 0.15595 | 35.9953 | 0.0126 | 32167 | 0.155 | 2924925 | 0.082458 | 13990.96 | 4.51 | 733.88 | 26605 | 537.55 | 4514.89 | 0
4 | 17404.38 | 5.44 | 972842.8 | 0.14965 | 35.9953 | 0 | 32340 | 0.173 | 3026805 | 0.10188 | 13996.4 | 5.44 | 733.86 | 26574 | 537.58 | 4514.89 | 0
5 | 17408.12 | 3.74 | 1093036 | 0.12019 | 35.9954 | 0.0001 | 32341 | 0.001 | 3107588 | 0.080783 | 14000.75 | 4.35 | 733.87 | 26590 | 537.61 | 4514.89 | 0
6 | 17414.06 | 5.94 | 1189458 | 0.096422 | 36.0274 | 0.032 | 32341 | 0 | 3208814 | 0.10123 | 14006.49 | 5.74 | 733.87 | 26590 | 537.64 | 4514.89 | 0
7 | 17418.79 | 4.73 | 1379335 | 0.18988 | 36.1055 | 0.0781 | 32502 | 0.161 | 3303810 | 0.094996 | 14011.31 | 4.82 | 733.87 | 6590 | 537.66 | 4514.89 | 0
8 | 17423.95 | 5.16 | 1498103 | 0.11877 | 36.1056 | 0.0001 | 32602 | 0.1 | 3402352 | 0.098542 | 14016.87 | 5.56 | 733.87 | 26590 | 537.7 | 4514.89 | 0
9 | 17429.62 | 5.67 | 1594636 | 0.096533 | 36.1057 | 0.0001 | 32761 | 0.159 | 3502415 | 0.10006 | 14022.55 | 5.68 | 733.85 | 26558 | 537.72 | 4514.89 | 0
10 | 17435.35 | 5.73 | 1889450 | 0.29481 | 36.1057 | 0 | 32912 | 0.151 | 3598950 | 0.096535 | 14028.08 | 5.53 | 733.81 | 26495 | 537.73 | 4514.89 | 0
11 | 17439.38 | 4.03 | 1939144 | 0.049694 | 36.1544 | 0.0487 | 32912 | 0 | 3678012 | 0.079062 | 14031.96 | 3.88 | 733.81 | 26495 | 537.73 | 4514.89 | 0
12 | 17443.36 | 3.98 | 2040237 | 0.10109 | 36.1544 | 0 | 32912 | 0 | 3775685 | 0.097673 | 14036.18 | 4.22 | 733.84 | 26542 | 537.84 | 4514.89 | 0
13 | 17447.76 | 4.4 | 2174908 | 0.13467 | 36.1634 | 0.009 | 33048 | 0.136 | 3841200 | 0.065515 | 14041.07 | 4.89 | 733.85 | 26558 | 537.96 | 4514.89 | 0
14 | 17453.05 | 5.29 | 2404636 | 0.22973 | 36.2206 | 0.0572 | 33204 | 0.156 | 3933905 | 0.092705 | 14046.24 | 5.17 | 733.82 | 26511 | 537.95 | 4514.89 | 0
15 | 17458.08 | 5.03 | 2519428 | 0.11479 | 36.2207 | 0.0001 | 33312 | 0.108 | 4026234 | 0.092329 | 14051.27 | 5.03 | 733.8 | 26479 | 537.93 | 4514.89 | 0
16 | 17462.12 | 4.04 | 2617349 | 0.097921 | 36.2207 | 0 | 33312 | 0 | 4082135 | 0.055901 | 14055.94 | 4.67 | 733.78 | 26448 | 537.91 | 4514.89 | 0
17 | 17467.35 | 5.23 | 2774752 | 0.1574 | 36.2208 | 0.0001 | 33312 | 0 | 4165829 | 0.083694 | 14060.9 | 4.96 | 733.76 | 26416 | 537.91 | 4514.89 | 0
18 | 17473.79 | 6.44 | 2944394 | 0.16964 | 36.2868 | 0.066 | 33438 | 0.126 | 4269609 | 0.10378 | 14066.63 | 5.73 | 733.75 | 26401 | 537.89 | 4514.89 | 0
19 | 17477.58 | 3.79 | 3034600 | 0.090206 | 36.2869 | 0.0001 | 33538 | 0.1 | 4351743 | 0.082134 | 14070.73 | 4.1 | 733.75 | 26901 | 537.88 | 4514.89 | 0
20 | 17482.72 | 5.14 | 3092367 | 0.057767 | 36.2869 | 0 | 33538 | 0 | 4450945 | 0.099202 | 14076.18 | 5.45 | 733.75 | 26401 | 537.88 | 4514.89 | 0
21 | 17487.51 | 4.79 | 3162255 | 0.069888 | 36.3554 | 0.0685 | 33538 | 0 | 4536508 | 0.085563 | 14081.42 | 5.24 | 733.75 | 26401 | 537.86 | 4514.89 | 0
22 | 17494.007 | 6.497 | 3258362 | 0.096107 | 36.3555 | 0.0001 | 33658 | 0.12 | 4631443 | 0.094935 | 14087.1 | 5.68 | 733.34 | 26385 | 537.85 | 4514.89 | 0
23 | 17497.76 | 3.753 | 3394885 | 0.13652 | 36.4174 | 0.0619 | 33718 | 0.06 | 4702409 | 0.070966 | 14091.86 | 4.76 | 733.73 | 26369 | 537.85 | 4514.89 | 0
24 | 17504.22 | 6.46 | 3506566 | 0.11168 | 36.4175 | 0.0001 | 33814 | 0.096 | 4795285 | 0.092876 | 14097.81 | 5.95 | 733.72 | 26354 | 537.83 | 4514.89 | 0
25 | 17509.68 | 5.46 | 3560875 | 0.054309 | 36.4176 | 0.0001 | 33814 | 0 | 4888559 | 0.093274 | 14103.31 | 5.5 | 733.65 | 26306 | 537.81 | 4514.89 | 0
26 | 17514.69 | 5.01 | 3723159 | 0.16228 | 36.4176 | 0 | 34082 | 0.268 | 4978471 | 0.089912 | 14108.51 | 5.2 | 733.8 | 26291 | 537.78 | 4514.89 | 0
27 | 17519.7 | 5.01 | 3840092 | 0.11693 | 36.4376 | 0.02 | 34082 | 0 | 5071259 | 0.092788 | 14113.84 | 5.33 | 733.65 | 26244 | 537.73 | 4514.89 | 0
28 | 17524.98 | 5.28 | 3873300 | 0.033208 | 36.5023 | 0.0647 | 34082 | 0 | 5161235 | 0.089976 | 14118.99 | 5.15 | 733.64 | 26228 | 537.7 | 4514.89 | 0
29 | 17530.75 | 5.77 | 4009529 | 0.13623 | 36.522 | 0.0197 | 34193 | 0.111 | 5257237 | 0.096002 | 14122.77 | 3.78 | 733.91 | 26653 | 537.85 | 4514.89 | 0
30 | 17535.32 | 4.57 | 4223689 | 0.21416 | 36.5908 | 0.0688 | 34200 | 0.007 | 5345935 | 0.088698 | 14127.93 | 5.16 | 733.97 | 26748 | 538.04 | 4514.889 | -0.001
31
Totals | 523841.347 | 152.46 |  | 3.8081 |  | 0.6655 |  | 2.426 |  | 2.6836 |  | 152.59 |  |  |  |  | -0.001
Average | 17461.3782 | 5.082 |  | 0.12694 |  | 0.022183 |  | 0.080867 |  | 0.089452 |  | 5.0863 | 733.7933 |  | 537.8153 |  | -3.3333e-05
Min |  | 3.74 |  | 0.033208 |  | 0 |  | 0 |  | 0.055901 |  | 3.78 | 733.34 |  | 537.55 |  | -0.001
Max |  | 6.55 |  | 0.29481 |  | 0.0781 |  | 0.268 |  | 0.10378 |  | 5.95 | 733.97 |  | 538.07 |  | 0
Calculated Values
| Raw Water Added To System (MG) |  |  | 148.6519 |  |  | Raw to Potable Differential |  |  | 1.1714
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 147.4804 |  |  | Average Raw for Month |  |  | 5.082
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.71664 |  |  | Peak Raw Flow for Month |  |  | 6.55
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | April/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 61 | 0 | 19.1667 | 8.88 | 2.3083 | 0.13367 | 8.49 | 8.7783 | 3.6217 | 150 | 160 | 110 | 104.6667 | 6.6667
2 | 66 | 0 | 19 | 9.76 | 2.7383 | 0.11433 | 8.38 | 8.7333 | 3.5148 | 150 | 153.3333 | 110 | 99.3333 | 5.6667
3 | 39 | 0.2 | 19 | 16 | 2.0575 | 0.13733 | 8.53 | 8.7433 | 3.8008 | 140 | 157 | 115 | 92 | 8
4 | 56 | 0.1 | 18.3333 | 9.43 | 2.3417 | 0.14933 | 8.45 | 8.855 | 3.8767 | 140 | 147 | 120 | 84.6667 | 7.6667
5 | 62 | 0 | 18.6667 | 10 | 1.9325 | 0.12817 | 8.42 | 8.7233 | 3.7075 | 140 | 148.6667 | 111 | 90.3333 | 2.3333
6 | 64 | 0.3 | 18.5 | 8.41 | 2.255 | 0.108 | 8.34 | 8.7767 | 3.6483 | 150 | 157.3333 | 115 | 107.6667 | 6
7 | 73 | 0 | 18.3333 | 10.1 | 2.832 | 0.122 | 8.41 | 8.7833 | 3.9533 | 144 | 155.3333 | 112 | 95 | 3.6667
8 | 70 | 0 | 19.5 | 10.5 | 1.72 | 0.11567 | 8.52 | 8.775 | 3.8167 | 160 | 153 | 110 | 96.6667 | 3.3333
9 | 59 | 0.1 | 19 | 14.3 | 1.8417 | 0.11717 | 8.92 | 8.8083 | 3.8342 | 149 | 152.6667 | 115 | 92.3333 | 6
10 | 63 | 0 | 19.5 | 10.3 | 1.9 | 0.088833 | 8.84 | 7.4978 | 3.8458 | 143 | 147.6667 | 114 | 90 | 5
11 | 70 | 0 | 19.5 | 6.83 | 1.724 | 0.102 | 8.43 | 8.7983 | 3.8408 | 143 | 152.3333 | 115 | 94.6667 | 4.6667
12 | 46 | 0.04 | 19.5 | 8.63 | 1.745 | 0.16467 | 8.76 | 8.7683 | 3.6933 | 151 | 153.6667 | 115 | 93.3333 | 5.3333
13 | 45 | 0 | 18.8333 | 13 | 1.496 | 0.149 | 8.48 | 8.8367 | 3.4825 | 147 | 148.3333 | 115 | 92.6667 | 7.3333
14 | 46 | 0 | 18 | 16.2 | 1.97 | 0.13383 | 8.69 | 8.81 | 3.5367 | 156 | 153.6667 | 119 | 91.6667 | 3.6667
15 | 50 | 0 | 17.5 | 11.3 | 2.08 | 0.1745 | 8.59 | 8.72 | 3.54 | 155 | 153.3333 | 113 | 92.3333 | 4.3333
16 | 81 | 0 | 18.1667 | 13.6 | 2.084 | 0.15867 | 8.43 | 8.8567 | 3.4592 | 162 | 153.6667 | 118 | 86.6667 | 6
17 | 62 | 0 | 20 | 22.1 | 1.998 | 0.12067 | 8.59 | 8.8617 | 2.3125 | 150 | 153.5 | 120 | 87 | 6
18 | 49 | 0 | 18 | 15.8 | 2.0533 | 0.1255 | 8.72 | 8.7917 | 3.435 | 156 | 157.3333 | 117 | 89.6667 | 4
19 | 64 | 0 | 18.6667 | 9.68 | 1.8 | 0.1555 | 8.63 | 8.645 | 3.5625 | 154 | 156.6667 | 118 | 97.6667 | 1.6667
20 | 59 | 0 | 18.6667 | 6.67 | 1.7883 | 0.10367 | 8.61 | 8.7333 | 3.4867 | 154 | 155.3333 | 122 | 95 | 5.3333
21 | 72 | 0 | 18.1667 | 6.67 | 1.998 | 0.10233 | 8.92 | 8.8083 | 3.8525 | 145 | 158.3333 | 116 | 91.6667 | 1
22 | 54 | 0 | 20 | 9.05 | 2.6533 | 0.14667 | 8.6 | 8.805 | 3.7042 | 153 | 158.6667 | 120 | 92.6667 | 3.3333
23 | 66 | 0 | 20 | 8.72 | 2.4033 | 0.1582 | 8.8 | 8.854 | 3.7375 | 154 | 150 | 116 | 85.3333 | 4
24 | 70 | 0 | 19 | 7.52 | 2.2633 | 0.15633 | 8.78 | 8.8033 | 3.7675 | 148 | 147 | 116 | 86.3333 | 4.3333
25 | 58 | 0 | 20.1667 | 8.39 | 1.7733 | 0.108 | 8.72 | 8.72 | 3.7575 | 147 | 155.3333 | 120 | 95.3333 | 6.6667
26 | 66 | 0 | 20.1667 | 9.42 | 1.8817 | 0.13017 | 8.67 | 8.75 | 3.5692 | 143 | 153 | 119 | 89.6667 | 3
27 | 72 | 0 | 20.5 | 9.47 | 1.8517 | 0.1295 | 8.62 | 8.8067 | 3.6867 | 157 | 148.3333 | 119 | 94 | 5.6667
28 | 65 | 0 | 21.3333 | 11.9 | 1.855 | 0.12783 | 8.57 | 8.7583 | 3.5825 | 167 | 148.3333 | 119 | 87.6667 | 5.3333
29 | 55 | 2 | 21.3333 | 6.79 | 1.742 | 0.17617 | 8.55 | 8.695 | 3.4492 | 154 | 149.6667 | 119 | 98.6667 | 4.3333
30 | 63 | 0 | 20.8 | 12.9 | 1.898 | 0.1762 | 8.6 | 8.656 | 3.568 | 149 | 155 | 118 | 96 | 5.3333
31 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
TOTAL |  | 2.74
AVG. | 58.9032 | 0.088387 | 19.2433 | 10.744 | 2.0328 | 0.1338 | 8.602 | 8.7318 | 3.6215 | 150.3667 | 153.1167 | 116.2 | 93.0222 | 4.8556
MAX. | 81 | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MIN. | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: April 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 4 | 24 | 106 | 0.51 | 95 | 1 | 51 | 2894.08 | 380 | 410.4 | 28 | 52.9789 | 7.5128 | 0.9336 | 6.9563 | 0.51257
2 | 4 | 24 | 96 | 0.48 | 143 | 1 | 45 | 1963.84 | 320 | 342 | 83 | 42.7355 | 7.4423 | 0.97925 | 6.9636 | 1.8062
3 | 4 | 17.5 | 99 | 0.96 | 155 | 1 | 32 | 1395.36 | 280 | 342 | 42 | 41.6192 | 10.2008 | 0.95446 | 8.3515 | 1.2527
4 | 3 | 24 | 105 | 0.05 | 173 | 1 | 44 | 1899.24 | 320 | 410.4 | 61 | 41.8615 | 9.0457 | 0.96981 | 7.0532 | 1.3445
5 | 3 | 15 | 0 | 0 | 0 | 0 | 27 | 1317.84 | 200 | 256.5 | 29 | 42.2498 | 8.2234 | 0.86562 | 6.412 | 0.92974
6 | 4 | 24 | 0 | 0 | 0 | 0 | 47 | 2306.22 | 380 | 495.9 | 93 | 46.5531 | 10.0102 | 0.94874 | 7.6706 | 1.8773
7 | 4 | 20 | 109 | 1.29 | 162 | 1 | 36 | 2164.1 | 220 | 453.15 | 19 | 54.8593 | 11.4872 | 0.91259 | 5.5769 | 0.48164
8 | 3 | 24 | 118 | 0.51 | 100 | 1 | 37 | 2306.22 | 300 | 367.65 | 7 | 53.5902 | 8.5432 | 0.85978 | 6.9712 | 0.16266
9 | 3 | 24 | 110 | 0.72 | 159 | 1 | 42 | 2577.54 | 320 | 384.75 | 19 | 54.5075 | 8.1363 | 0.88818 | 6.7671 | 0.40179
10 | 3 | 24 | 103 | 0.51 | 151 | 1 | 42 | 2674.44 | 340 | 427.5 | 30 | 55.9644 | 8.9457 | 0.87888 | 7.1147 | 0.62777
11 | 3 | 19 | 0 | 0 | 0 | 0 | 29 | 1744.2 | 100 | 299.25 | 72 | 51.895 | 8.9035 | 0.86283 | 2.9753 | 2.1422
12 | 3 | 19 | 0 | 0 | 0 | 0 | 29 | 1369.52 | 440 | 299.25 | 35 | 41.2591 | 9.0154 | 0.87367 | 13.2557 | 1.0544
13 | 3 | 21.75 | 99 | 0.49 | 136 | 1 | 39 | 1589.16 | 320 | 324.9 | 20 | 43.3061 | 8.8538 | 1.0628 | 8.7203 | 0.54502
14 | 3 | 24 | 90 | 0.51 | 156 | 1 | 44 | 1815.26 | 360 | 342 | 43 | 41.145 | 7.7518 | 0.99731 | 8.1598 | 0.97465
15 | 3 | 24 | 99 | 0.96 | 108 | 1 | 48 | 1744.2 | 340 | 384.75 | 12 | 41.5779 | 9.1716 | 1.1442 | 8.1048 | 0.28605
16 | 3 | 16.75 | 0 | 0 | 0 | 0 | 38 | 1388.9 | 280 | 282.15 | 29 | 41.2215 | 8.374 | 1.1278 | 8.3102 | 0.8607
17 | 4 | 20 | 0 | 0 | 0 | 0 | 44 | 1854.02 | 400 | 384.75 | 26 | 42.5057 | 8.8209 | 1.0088 | 9.1705 | 0.59608
18 | 4 | 24 | 105 | 1.96 | 126 | 1 | 59 | 2403.12 | 440 | 495.9 | 33 | 44.7428 | 9.233 | 1.0985 | 8.1922 | 0.61442
19 | 3 | 18.5 | 136 | 0.68 | 100 | 1 | 34 | 1589.16 | 200 | 256.5 | 7 | 50.2762 | 8.1149 | 1.0757 | 6.3274 | 0.22146
20 | 3 | 24 | 0 | 0 | 0 | 0 | 52 | 2118.88 | 380 | 367.65 | 15 | 49.4285 | 8.5764 | 1.213 | 8.8645 | 0.34991
21 | 4 | 19.5 | 0 | 0 | 0 | 0 | 39 | 1821.72 | 280 | 299.25 | 41 | 45.6016 | 7.4909 | 0.97625 | 7.009 | 1.0263
22 | 4 | 24 | 114 | 0.96 | 120 | 1 | 52 | 2403.12 | 340 | 470.25 | 27 | 44.3503 | 8.6786 | 0.95968 | 6.2748 | 0.49829
23 | 4 | 15 | 120 | 1.23 | 60 | 1 | 29 | 1298.46 | 200 | 282.15 | 11 | 41.4843 | 9.0144 | 0.92652 | 6.3898 | 0.35144
24 | 4 | 24 | 134 | 0.47 | 96 | 1 | 52 | 2377.28 | 360 | 470.25 | 15 | 44.1247 | 8.7283 | 0.96517 | 6.682 | 0.27842
25 | 3 | 24 | 0 | 0 | 0 | 0 | 41 | 1950.92 | 300 | 384.75 | 51 | 42.8431 | 8.4493 | 0.90038 | 6.5881 | 1.12
26 | 3 | 24 | 91 | 49 | 248 | 2 | 40 | 1834.64 | 260 | 410.4 | 27 | 43.9083 | 9.8221 | 0.95732 | 6.2226 | 0.64619
27 | 3 | 24 | 0 | 0 | 0 | 0 | 39 | 1375.98 | 260 | 384.75 | 35 | 32.9313 | 9.2082 | 0.93339 | 6.2226 | 0.83765
28 | 4 | 24 | 0 | 0 | 0 | 0 | 42 | 1821.72 | 300 | 342 | 43 | 41.3696 | 7.7665 | 0.95378 | 6.8127 | 0.97649
29 | 4 | 20.25 | 141 | 1.62 | 111 | 1 | 45 | 2028.44 | 360 | 410.4 | 18 | 42.1522 | 8.5284 | 0.93513 | 7.481 | 0.37405
30 | 3 | 20 | 0 | 0 | 0 | 0 | 39 | 1589.16 | 100 | 342 | 14 | 41.6951 | 8.9731 | 1.0233 | 2.6237 | 0.36732
31 | [6 empty] | 0 | 0 | 0 |  | 0 | #VALUE! | #VALUE! | 0 | 0 | 0
TOTAL |  | 650.25 |  |  | 2399 | 19 | 1237 | 57616.74 | 9080 | 11123.55 | 985
AVG | 3.4333 |  | 65.8333 | 2.097 | 79.9667 | 0.63333 | 39.9032 | 2113.0073 | 292.9032 | 380.8636 | 32.8333 | 43.3909 | 8.7674 | 0.94149 | 6.9105 | 0.75864
MIN | 3 |  | 0 | 0 | 0 | 0 | 0 | 1317.84 | 0 | 256.5 | 7 | 32.9313 | #VALUE! | 0 | 0 | 0
MAX | 4 |  | 141 | 49 | 248 | 2 | 59 | 2894.08 | 440 | 495.9 | 93 | 51.895 | #VALUE! | 1.213 | 13.2557 | 2.1422

## Monthly Chemical Report
Month, Year: |  | April/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #REF!
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 6.55 | 521.73 | 8.5229 | 55.8251 | 5788.16 | 83.5086 | 546.9811 | 380 | 20.8565 | 136.61 | 410.4 | 45.7392 | 299.592 | [9 empty] | 28 | 8.9536 | 58.646 | 216.15 | 167.5808 | 1313.8042
2 | 5.51 | 460.35 | 8.9396 | 49.2574 | 3927.68 | 67.3622 | 371.1658 | 320 | 20.8784 | 115.04 | 342 | 45.3103 | 249.66 | [9 empty] | 83 | 31.5505 | 173.8435 | 181.83 | 174.0411 | 1140.7967
3 | 4.02 | 327.36 | 8.7133 | 35.0275 | 2790.72 | 65.6027 | 263.723 | 280 | 25.0398 | 100.66 | 342 | 62.1045 | 249.66 | [9 empty] | 42 | 21.8828 | 87.969 | 132.66 | 183.3432 | 869.6996
4 | 5.44 | 450.12 | 8.8535 | 48.1628 | 3798.48 | 65.9846 | 358.9564 | 320 | 21.1471 | 115.04 | 410.4 | 55.0721 | 299.592 | [9 empty] | 61 | 23.4861 | 127.7645 | 179.52 | 174.5433 | 1129.0357
5 | 3.74 | 276.21 | 7.9023 | 29.5545 | 2635.68 | 66.5967 | 249.0718 | 200 | 19.2246 | 71.9 | 256.5 | 50.0655 | 187.245 | [9 empty] | 29 | 16.2408 | 60.7405 | 123.42 | 160.0299 | 721.9317
6 | 5.94 | 480.81 | 8.6611 | 51.4467 | 4612.44 | 73.3797 | 435.8756 | 380 | 22.9983 | 136.61 | 495.9 | 60.9439 | 362.007 | [9 empty] | 93 | 32.7927 | 194.7885 | 196.02 | 198.7757 | 1376.7478
7 | 4.73 | 368.28 | 8.3311 | 39.406 | 4328.2 | 86.4725 | 409.0149 | 220 | 16.7209 | 79.09 | 453.15 | 69.9365 | 330.7995 | [9 empty] | 19 | 8.4134 | 39.7955 | 156.09 | 189.8744 | 1054.1959
8 | 5.16 | 378.51 | 7.8489 | 40.5006 | 4612.44 | 84.472 | 435.8756 | 300 | 20.9012 | 107.85 | 367.65 | 52.0125 | 268.3845 | [9 empty] | 7 | 2.8414 | 14.6615 | 170.28 | 168.076 | 1037.5521
9 | 5.67 | 429.66 | 8.1082 | 45.9736 | 5155.08 | 85.918 | 487.1551 | 320 | 20.2892 | 115.04 | 384.75 | 49.5357 | 280.8675 | [9 empty] | 19 | 7.0186 | 39.7955 | 187.11 | 170.8698 | 1155.9417
10 | 5.73 | 429.66 | 8.0233 | 45.9736 | 5348.88 | 88.2145 | 505.4692 | 340 | 21.3316 | 122.23 | 427.5 | 54.4634 | 312.075 | [9 empty] | 30 | 10.966 | 62.835 | 189.09 | 182.9987 | 1237.6728
11 | 4.03 | 296.67 | 7.8768 | 31.7437 | 3488.4 | 81.8 | 329.6538 | 100 | 8.9206 | 35.95 | 299.25 | 54.2066 | 218.4525 | [9 empty] | 72 | 37.4203 | 150.804 | 132.99 | 190.2243 | 899.594
12 | 3.98 | 296.67 | 7.9758 | 31.7437 | 2739.04 | 65.035 | 258.8393 | 440 | 39.7437 | 158.18 | 299.25 | 54.8876 | 218.4525 | [9 empty] | 35 | 18.419 | 73.3075 | 131.34 | 186.061 | 871.863
13 | 4.4 | 398.97 | 9.7022 | 42.6898 | 3178.32 | 68.2616 | 300.3512 | 320 | 26.1455 | 115.04 | 324.9 | 53.9039 | 237.177 | [9 empty] | 20 | 9.5205 | 41.89 | 145.2 | 167.5336 | 882.348
14 | 5.29 | 450.12 | 9.1045 | 48.1628 | 3630.52 | 64.8552 | 343.0841 | 360 | 24.465 | 129.42 | 342 | 47.1947 | 249.66 | [9 empty] | 43 | 17.0252 | 90.0635 | 174.57 | 162.6447 | 1034.9605
15 | 5.03 | 491.04 | 10.4456 | 52.5413 | 3488.4 | 65.5375 | 329.6538 | 340 | 24.3002 | 122.23 | 384.75 | 55.8385 | 280.8675 | [9 empty] | 12 | 4.9968 | 25.134 | 165.99 | 161.1186 | 976.4166
16 | 4.04 | 388.74 | 10.2958 | 41.5952 | 2777.8 | 64.9758 | 262.5021 | 280 | 24.9158 | 100.66 | 282.15 | 50.9825 | 205.9695 | [9 empty] | 29 | 15.0348 | 60.7405 | 133.32 | 166.2048 | 804.7873
17 | 5.23 | 450.12 | 9.209 | 48.1628 | 3708.04 | 67 | 350.4098 | 400 | 27.4952 | 143.8 | 384.75 | 53.7032 | 280.8675 | [9 empty] | 26 | 10.4124 | 54.457 | 172.59 | 167.8197 | 1050.2871
18 | 6.44 | 603.57 | 10.0283 | 64.582 | 4806.24 | 70.5263 | 454.1897 | 440 | 24.5621 | 158.18 | 495.9 | 56.2123 | 362.007 | [9 empty] | 33 | 10.7327 | 69.1185 | 212.52 | 172.0617 | 1320.5972
19 | 3.79 | 347.82 | 9.8197 | 37.2167 | 3178.32 | 79.2483 | 300.3512 | 200 | 18.971 | 71.9 | 256.5 | 49.405 | 187.245 | [9 empty] | 7 | 3.8685 | 14.6615 | 125.07 | 161.3125 | 736.4445
20 | 5.14 | 531.96 | 11.0739 | 56.9197 | 4237.76 | 77.9121 | 400.4683 | 380 | 26.5778 | 136.61 | 367.65 | 52.2149 | 268.3845 | [9 empty] | 15 | 6.1124 | 31.4175 | 169.62 | 173.8911 | 1063.42
21 | 4.79 | 398.97 | 8.9123 | 42.6898 | 3643.44 | 71.88 | 344.3051 | 280 | 21.0146 | 100.66 | 299.25 | 45.6059 | 218.4525 | [9 empty] | 41 | 17.9279 | 85.8745 | 158.07 | 165.3407 | 950.0519
22 | 6.497 | 531.96 | 8.7609 | 56.9197 | 4806.24 | 69.9076 | 454.1897 | 340 | 18.8133 | 122.23 | 470.25 | 52.8371 | 343.2825 | [9 empty] | 27 | 8.7042 | 56.5515 | 214.401 | 159.0231 | 1247.5744
23 | 3.753 | 296.67 | 8.4582 | 31.7437 | 2596.92 | 65.3901 | 245.4089 | 200 | 19.158 | 71.9 | 282.15 | 54.8813 | 205.9695 | [9 empty] | 11 | 6.139 | 23.0395 | 123.849 | 154.0265 | 701.9106
24 | 6.46 | 531.96 | 8.8111 | 56.9197 | 4754.56 | 69.552 | 449.3059 | 360 | 20.0341 | 129.42 | 470.25 | 53.1397 | 343.2825 | [9 empty] | 15 | 4.8634 | 31.4175 | 213.18 | 156.4003 | 1223.5256
25 | 5.46 | 419.43 | 8.2196 | 44.879 | 3901.84 | 67.5318 | 368.7239 | 300 | 19.7527 | 107.85 | 384.75 | 51.4409 | 280.8675 | [9 empty] | 51 | 19.564 | 106.8195 | 180.18 | 166.5091 | 1089.3199
26 | 5.01 | 409.2 | 8.7394 | 43.7844 | 3669.28 | 69.211 | 346.747 | 260 | 18.6567 | 93.47 | 410.4 | 59.7988 | 299.592 | [9 empty] | 27 | 11.2877 | 56.5515 | 165.33 | 167.6936 | 1005.4749
27 | 5.01 | 398.97 | 8.5209 | 42.6898 | 2751.96 | 51.9082 | 260.0602 | 260 | 18.6567 | 93.47 | 384.75 | 56.0614 | 280.8675 | [9 empty] | 35 | 14.6322 | 73.3075 | 165.33 | 149.7794 | 915.725
28 | 5.28 | 429.66 | 8.7071 | 45.9736 | 3643.44 | 65.2093 | 344.3051 | 300 | 20.4261 | 107.85 | 342 | 47.2841 | 249.66 | [9 empty] | 43 | 17.0575 | 90.0635 | 174.24 | 158.6841 | 1012.0922
29 | 5.77 | 460.35 | 8.5368 | 49.2574 | 4056.88 | 66.4428 | 383.3752 | 360 | 22.4298 | 129.42 | 410.4 | 51.9224 | 299.592 | [9 empty] | 18 | 6.534 | 37.701 | 190.41 | 155.8658 | 1089.7556
30 | 4.57 | 398.97 | 9.3413 | 42.6898 | 3178.32 | 65.7224 | 300.3512 | 100 | 7.8665 | 35.95 | 342 | 54.6302 | 249.66 | [9 empty] | 14 | 6.4164 | 29.323 | 150.81 | 143.9768 | 808.784
31 |  | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 |  | #VALUE! | #VALUE! | [9 empty] | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE!
Total | 152.46 |  |  | 1354.0326 |  |  | 10889.5639 |  |  | 3264.26 |  |  | #VALUE! |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 2063.0825 | 5031.18 | 5056.3045 | 30722.3104
Avg. | 5.082 | 408.21 | 8.8815 | 43.6785 | 3717.209 | 71.1806 | 351.2763 | 292.9032 | 21.4098 | 105.2987 | 370.785 | 53.3778 | 270.6731 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 31.7742 | 13.6938 | 66.551 | 167.706 | 201.5106 | 1024.077
Max | 6.55 | 603.57 | #VALUE! | 64.582 | 5788.16 | #VALUE! | 546.9811 | 440 | #VALUE! | 158.18 | 495.9 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | #VALUE! | 194.7885 | #VALUE! | #VALUE! | #VALUE!
Min. | 3.74 | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 | 256.5 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE!
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 2.0945 | Lime | 33 | Per MGD
|  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract |  | 0.20151 | PerKG

## LAS Meter
Month:
LAS Carrier Water Meter
Prev. | 9399840
1 | 9440540 | 40700
2 | 9481370 | 40830
3 | 9510500 | 29130
4 | 9550570 | 40070
5 | 9578330 | 27760
6 | 9618490 | 40160
7 | 9651810 | 33320
8 | 9692260 | 40450
9 | 9732700 | 40440
10 | 9772990 | 40290
11 | 9804960 | 31970
12 | 9836660 | 31700
13 | 9873060 | 36400
14 | 9913670 | 40610
15 | 9953860 | 40190
16 | 9961800 | 7940
17 | 9997310 | 35510
18 | 10037910 | 40600
19 | 10068260 | 30350
20 | 10108740 | 40480
21 | 10142080 | 33340
22 | 10182610 | 40530
23 | 10208480 | 25870
24 | 10248240 | 39760
25 | 10288740 | 40500
26 | 10328650 | 39910
27 | 10369060 | 40410
28 | 10407410 | 38350
29 | 10449240 | 41830
30 | 10482760 | 33520
31 | 10482760 | 0
Total |  | 1082920

## Graphs
Chemicals | Amount
LAS | 2021.7447
Fe | 10889.5639
CL2 | 3264.26
Poly | #VALUE!
Potassium | 2063.0825
Lime | 0
Chemfloc 3315 | 30722.3104