## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: December 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 18989.04 | 6.96 | 17895159 | 0.1805 | 42.0636 | 0 | 56951 | 0.128 | 13283758 | 0.1526 | 1489.261 | 6.703 | 731.11 | 22352 | 536.35 | 5137.96 | .-10
1 | 18994.45 | 5.41 | 18035688 | 0.14053 | 42.0637 | 0.0001 | 57103 | 0.152 | 13428900 | 0.14514 | 1494.958 | 5.697 | 731.08 | 22308 | 536.29 | 5137.87 | -0.09
2 | 18999.41 | 4.96 | 18291189 | 0.2555 | 42.1369 | 0.0732 | 57201 | 0.098 | 13575400 | 0.1465 | 1500.03 | 5.072 | 731.07 | 22293 | 536.28 | 5137.84 | -0.03
3 | 19004.66 | 5.25 | 18291189 | 0 | 42.137 | 0.0001 | 57201 | 0 | 13723879 | 0.14848 | 1505.504 | 5.474 | 731.04 | 22248 | 536.25 | 5137.89 | 0.05
4 | 19011.41 | 6.75 | 18495758 | 0.20457 | 42.1699 | 0.0329 | 57364 | 0.163 | 13872282 | 0.1484 | 1512.125 | 6.621 | 731.02 | 22218 | 536.24 | 5137.93 | 0.04
5 | 19017.08 | 5.67 | 18780488 | 0.28473 | 42.1699 | 0 | 57578 | 0.214 | 14017600 | 0.14532 | 1517.767 | 5.642 | 731.01 | 22203 | 536.23 | 5137.97 | 0.04
6 | 19022.11 | 5.03 | 18841228 | 0.06074 | 42.17 | 0.0001 | 57578 | 0 | 14168535 | 0.15094 | 1523.333 | 5.566 | 731 | 22188 | 536.23 | 5138.01 | 0.04
7 | 19027.93 | 5.82 | 18888480 | 0.047252 | 42.1895 | 0.0195 | 57710 | 0.132 | 14316600 | 0.14807 | 1529.312 | 5.979 | 730.97 | 22143 | 536.22 | 5138.05 | 0.04
8 | 19034.31 | 6.38 | 19033146 | 0.14467 | 42.1896 | 0.0001 | 57710 | 0 | 14461250 | 0.14465 | 1535.791 | 6.479 | 730.95 | 22114 | 536.2 | 5138.1 | 0.05
9 | 19039.88 | 5.57 | 19182494 | 0.14935 | 42.2626 | 0.073 | 57837 | 0.127 | 14608426 | 0.14718 | 1541.726 | 5.935 | 730.94 | 22099 | 536.2 | 5138.14 | 0.04
10 | 19046.23 | 6.35 | 19182494 | 0 | 42.3019 | 0.0393 | 57837 | 0 | 14753311 | 0.14489 | 1548.014 | 6.288 | 730.92 | 22069 | 536.18 | 5138.17 | 0.03
11 | 19052.13 | 5.9 | 19422986 | 0.24049 | 42.302 | 0.0001 | 57944 | 0.107 | 14900793 | 0.14748 | 1553.74 | 5.726 | 730.8 | 21920 | 536.2 | 5138.21 | 0.04
12 | 19057.08 | 4.95 | 19568400 | 0.14541 | 42.3098 | 0.0078 | 58037 | 0.093 | 15044445 | 0.14365 | 1558.956 | 5.216 | 730.81 | 21905 | 536.2 | 5138.25 | 0.04
13 | 19062.2 | 5.12 | 19671010 | 0.10261 | 42.326 | 0.0162 | 58171 | 0.134 | 15198744 | 0.1543 | 1564.112 | 5.156 | 730.9 | 22039 | 536.22 | 5138.28 | 0.03
14 | 19067.13 | 4.93 | 19812564 | 0.14155 | 42.326 | 0 | 58171 | 0 | 15342699 | 0.14395 | 1569.55 | 5.438 | 730.94 | 22099 | 536.21 | 5138.32 | 0.04
15 | 19072.2 | 5.07 | 19957794 | 0.14523 | 42.3261 | 0.0001 | 58317 | 0.146 | 15505420 | 0.16272 | 1574.795 | 5.245 | 730.92 | 22069 | 536.19 | 5138.35 | 0.03
16 | 19078.31 | 6.11 | 20276965.2 | 0.31917 | 42.3926 | 0.0665 | 58466 | 0.149 | 15654429 | 0.14901 | 1580.886 | 6.091 | 730.9 | 22039 | 536.18 | 5138.4 | 0.05
17 | 19084.38 | 6.07 | 20447768.5 | 0.1708 | 42.3926 | 0 | 58589 | 0.123 | 15801672 | 0.14724 | 1586.926 | 6.04 | 730.89 | 22024 | 536.17 | 5138.43 | 0.03
18 | 19089.96 | 5.58 | 20558871 | 0.1111 | 42.4185 | 0.0259 | 58697 | 0.108 | 15951482 | 0.14981 | 1592.464 | 5.538 | 730.87 | 21994 | 536.15 | 5138.47 | 0.04
19 | 19094.96 | 5 | 20599750.1 | 0.040879 | 42.452 | 0.0335 | 58697 | 0 | 16095145 | 0.14366 | 1597.977 | 5.513 | 730.87 | 21994 | 536.16 | 5138.51 | 0.04
20 | 19100.03 | 5.07 | 20677815.7 | 0.078066 | 42.4522 | 0.0002 | 58819 | 0.122 | 16244975 | 0.14983 | 1603.31 | 5.333 | 730.86 | 21979 | 536.16 | 5138.55 | 0.04
21 | 19104.99 | 4.96 | 20772417.2 | 0.094602 | 42.4523 | 0.0001 | 58819 | 0 | 16386720 | 0.14175 | 1608.204 | 4.894 | 730.85 | 21965 | 536.15 | 5138.59 | 0.04
22 | 19110.06 | 5.07 | 20890415.8 | 0.118 | 42.4523 | 0 | 58912 | 0.093 | 16534052 | 0.14733 | 1613.414 | 5.21 | 730.83 | 21935 | 536.13 | 5138.63 | 0.04
23 | 19115.13 | 5.07 | 21062528 | 0.17211 | 42.4524 | 0.0001 | 59037 | 0.125 | 16678310 | 0.14426 | 1618.777 | 5.363 | 730.84 | 21950 | 536.15 | 5138.68 | 0.05
24 | 19120.23 | 5.1 | 21062528 | 0 | 42.4524 | 0 | 59037 | 0 | 16833198 | 0.15489 | 1624.149 | 5.372 | 730.81 | 21905 | 536.13 | 5138.74 | 0.06
25 | 19125.63 | 5.4 | 21153399 | 0.090871 | 42.4525 | 0.0001 | 59125 | 0.088 | 16978350 | 0.14515 | 1629.563 | 5.414 | 730.78 | 21860 | 536.1 | 5138.79 | 0.05
26 | 19131.03 | 5.4 | 21257958 | 0.10456 | 42.5179 | 0.0654 | 59152 | 0.027 | 17124590 | 0.14624 | 1634.655 | 5.092 | 730.76 | 21831 | 536.09 | 5138.84 | 0.05
27 | 19136.03 | 5 | 21633529 | 0.37557 | 42.536 | 0.0181 | 59451 | 0.299 | 17270700 | 0.14611 | 1640.066 | 5.411 | 730.75 | 21816 | 536.08 | 5138.89 | 0.05
28 | 19141.02 | 4.99 | 21745194 | 0.11167 | 42.5361 | 0.0001 | 59582 | 0.131 | 17416563 | 0.14586 | 1645.166 | 5.1 | 730.74 | 21801 | 536.09 | 5138.94 | 0.05
29 | 19145.98 | 4.96 | 21824356 | 0.079162 | 42.579 | 0.0429 | 59582 | 0 | 17564065 | 0.1475 | 1650.04 | 4.874 | 730.72 | 21771 | 536.06 | 5138.99 | 0.05
30 | 19150.94 | 4.96 | 21991138 | 0.16678 | 42.5799 | 0.0009 | 59696 | 0.114 | 17715684 | 0.15162 | 1655.156 | 5.116 | 730.74 | 21801 | 536.03 | 5139.03 | 0.04
31 | 19155.45 | 4.51 | 22102750 | 0.11161 | 42.58 | 0.0001 | 59809 | 0.113 | 17861839 | 0.14616 | 1659.816 | 4.66 | 730.81 | 21905 | 536.22 | 5139.08 | 0.05
Totals | 591392.34 | 166.41 |  | 4.2076 |  | 0.5164 |  | 2.858 |  | 4.5781 |  | 170.555 |  |  |  |  | 1.12
Average | 19077.1723 | 5.3681 |  | 0.13573 |  | 0.016658 |  | 0.092194 |  | 0.14768 |  | 5.5018 | 730.8835 |  | 536.1739 |  | 0.036129
Min |  | 4.51 |  | 0 |  | 0 |  | 0 |  | 0.14175 |  | 4.66 | 730.72 |  | 536.03 |  | -0.09
Max |  | 6.75 |  | 0.37557 |  | 0.0732 |  | 0.299 |  | 0.16272 |  | 6.621 | 731.08 |  | 536.29 |  | 0.06
Calculated Values
| Raw Water Added To System (MG) |  |  | 162.2024 |  |  | Raw to Potable Differential |  |  | -0.91651
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 163.1189 |  |  | Average Raw for Month |  |  | 5.3681
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.83319 |  |  | Peak Raw Flow for Month |  |  | 6.75
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | December/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 45 | 0 | 15.6667 | 11.3 | 2.385 | 0.12183 | 8.42 | 9.0467 | 3.6 | 125 | 135.6667 | 91 | 75.6667 | 3.6667
2 | 40 | 0 | 15.6667 | 8.89 | 2.2183 | 0.097167 | 8.41 | 8.9283 | 3.81 | 120 | 130.3333 | 92 | 69 | 5.3333
3 | 30 | 0 | 14.1667 | 11.1 | 2.4333 | 0.10017 | 8.47 | 9.1517 | 3.8233 | 124 | 133.6667 | 96 | 67.6667 | 4.3333
4 | 37 | 0 | 13.6667 | 10.2 | 2.1783 | 0.092 | 8.55 | 8.9867 | 3.7417 | 132 | 128.6667 | 91 | 70.3333 | 2.6667
5 | 51 | 0 | 15.1667 | 9.89 | 2.5033 | 0.10467 | 8.5 | 8.9333 | 3.9567 | 125 | 139.3333 | 89 | 68.3333 | 4.3333
6 | 44 | 0 | 16.8333 | 9.66 | 2.4467 | 0.11617 | 8.68 | 9.0633 | 3.7808 | 120 | 131.6667 | 88 | 62 | 8
7 | 43 | 0 | 14 | 7.77 | 2.3317 | 0.081833 | 8.54 | 8.9783 | 3.5083 | 142 | 138.6667 | 85 | 64.3333 | 5.6667
8 | 44 | 0 | 13 | 7.06 | 2.3367 | 0.097667 | 8.75 | 8.9417 | 3.9 | 130 | 138.3333 | 102 | 76 | 2.3333
9 | 51 | 0 | 15.3333 | 6.76 | 2.1717 | 0.125 | 8.8 | 8.8033 | 3.7925 | 125 | 95.6667 | 87 | 73.6667 | 3
10 | 61 | 0 | 13.8333 | 7.77 | 2.44 | 0.091667 | 7.93 | 8.9167 | 3.6517 | 151 | 140.3333 | 82 | 67 | 6
11 | 39 | 1 | 14.1667 | 9.54 | 2.1967 | 0.0865 | 8.35 | 8.7367 | 3.9242 | 135 | 133.3333 | 88 | 69 | 4.3333
12 | 44 | 0 | 15.6667 | 8.04 | 2.16 | 0.081 | 8.25 | 8.7667 | 3.5142 | 132 | 137 | 88 | 69 | 8.3333
13 | 37 | 1 | 14.8333 | 6.37 | 2.72 | 0.0855 | 8.34 | 8.8983 | 3.6892 | 140 | 135.6667 | 82 | 67.6667 | 5
14 | 38 | 0 | 14.8333 | 7.43 | 2.6767 | 0.0805 | 8.35 | 8.975 | 3.6883 | 130 | 133.3333 | 90 | 67.3333 | 6.3333
15 | 40 | 0 | 13.8333 | 9.93 | 2.5 | 0.086167 | 8.83 | 8.89 | 3.8642 | 138 | 138 | 91 | 68.6667 | 4.3333
16 | 81 | 0 | 15 | 6.75 | 2.1217 | 0.10083 | 8.43 | 8.7867 | 3.9467 | 146 | 133.3333 | 90 | 70.6667 | 4
17 | 39 | 0 | 12.5 | 10.6 | 2.7433 | 0.094333 | 8.37 | 9.0533 | 3.7967 | 148 | 137 | 91 | 70.6667 | 5
18 | 55 | 0 | 12.3333 | 8.37 | 2.3067 | 0.091 | 8.36 | 8.7867 | 3.7158 | 140 | 140.3333 | 91 | 72.6667 | 3.3333
19 | 39 | 0 | 14 | 8.22 | 2.3833 | 0.086667 | 8.43 | 8.98 | 3.6708 | 156 | 139.6667 | 86 | 73.3333 | 6
20 | 38 | 0 | 13.6667 | 6.28 | 2.65 | 0.097833 | 8.52 | 8.9683 | 3.8592 | 162 | 148 | 88 | 71.3333 | 3.6667
21 | 49 | 0 | 13.3333 | 6.28 | 2.4017 | 0.117 | 8.61 | 9.0667 | 3.9817 | 138 | 131.3333 | 90 | 64.6667 | 5.6667
22 | 61 | 0 | 12.6667 | 7.26 | 2.47 | 0.095333 | 8.29 | 9.0617 | 3.8175 | 143 | 134 | 92 | 65 | 5.3333
23 | 38 | 0 | 15 | 6.87 | 2.5783 | 0.089333 | 8.48 | 8.9667 | 3.765 | 135 | 144 | 95 | 71.3333 | 4.6667
24 | 36 | 0 | 13.5 | 5.75 | 2.7483 | 0.093833 | 8.62 | 9.0983 | 3.6908 | 149 | 136 | 85 | 64 | 5.3333
25 | 46 | 0 | 15.1667 | 8.62 | 2.4983 | 0.083667 | 8.56 | 8.8467 | 3.7242 | 140 | 139 | 96 | 70 | 3
26 | 52 | 0 | 13.5 | 7.44 | 2.6817 | 0.099833 | 8.62 | 9.0183 | 3.7942 | 143 | 142.3333 | 105 | 70.3333 | 6.3333
27 | 50 | 0 | 12.8333 | 7.68 | 2.3017 | 0.0965 | 8.6 | 8.9183 | 3.7825 | 140 | 136.3333 | 93 | 69.3333 | 2.3333
28 | 57 | 0 | 12.5 | 6.83 | 2.6767 | 0.088833 | 8.48 | 9.0333 | 3.9658 | 139 | 135 | 96 | 65 | 4.6667
29 | 63 | 0.1 | 14.1667 | 6.59 | 2.53 | 0.107 | 8.49 | 8.935 | 3.7792 | 148 | 133 | 90 | 73.3333 | 4
30 | 37 | 2 | 14.1667 | 6.67 | 2.3933 | 0.1 | 8.46 | 8.95 | 3.7842 | 130 | 135.3333 | 91 | 74.3333 | 5.3333
31 | 34 | 1.5 | 12.8333 | 7.25 | 2.4817 | 0.087667 | 8.51 | 8.935 | 3.8142 | 145 | 138.3333 | 95 | 69.6667 | 4.6667
TOTAL |  | 5.6
AVG. | 45.7742 | 0.18065 | 14.1237 | 8.0377 | 2.4408 | 0.096048 | 8.4839 | 8.9491 | 3.7785 | 137.7742 | 135.2473 | 90.8387 | 69.3978 | 4.7419
MAX. | 81 | 2 | 16.8333 | 11.3 | 2.7483 | 0.125 | 8.83 | 9.1517 | 3.9817 | 162 | 148 | 105 | 76 | 8.3333
MIN. | 30 | 0 | 12.3333 | 5.75 | 2.1217 | 0.0805 | 7.93 | 8.7367 | 3.5083 | 120 | 95.6667 | 82 | 62 | 2.3333

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: December 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 4 | 24 | 144 | 0.48 | 152 | 1 | 46 | 1705.44 | 340 | 384.75 | 27 | 37.7984 | 8.5274 | 1.0195 | 7.5356 | 0.59841
2 | 4 | 24 | 115 | 0.47 | 98 | 1 | 43 | 1640.84 | 220 | 367.65 | 0 | 39.666 | 8.8876 | 1.0395 | 5.3183 | 0
3 | 4 | 24 | 0 | 0 | 0 | 0 | 43 | 1576.24 | 340 | 453.15 | 33 | 35.9995 | 10.3494 | 0.98207 | 7.7652 | 0.75368
4 | 4 | 24 | 121 | 2.31 | 163 | 1 | 57 | 2164.1 | 140 | 538.65 | 15 | 38.4421 | 9.5683 | 1.0125 | 2.4869 | 0.26645
5 | 4 | 24 | 105 | 0.72 | 214 | 2 | 48 | 1821.72 | 500 | 624.15 | 10 | 38.5241 | 13.199 | 1.0151 | 10.5736 | 0.21147
6 | 4 | 24 | 0 | 0 | 0 | 0 | 43 | 1589.16 | 280 | 427.5 | 20 | 37.8821 | 10.1907 | 1.025 | 6.6746 | 0.47676
7 | 4 | 24 | 125 | 4.47 | 132 | 1 | 54 | 1821.72 | 360 | 470.25 | 5 | 37.5312 | 9.6881 | 1.1125 | 7.4167 | 0.10301
8 | 4 | 24 | 0 | 0 | 0 | 0 | 59 | 2080.12 | 360 | 470.25 | 25 | 39.0932 | 8.8378 | 1.1088 | 6.7657 | 0.46984
9 | 4 | 24 | 131 | 0.67 | 127 | 1 | 46 | 1770.04 | 300 | 427.5 | 30 | 38.1032 | 9.2027 | 0.99023 | 6.458 | 0.6458
10 | 5 | 24 | 0 | 0 | 0 | 0 | 53 | 2034.9 | 480 | 513 | 35 | 38.4241 | 9.6867 | 1.0008 | 9.0636 | 0.66089
11 | 5 | 24 | 150 | 0.48 | 107 | 1 | 46 | 1892.78 | 160 | 410.4 | 28 | 38.4664 | 8.3404 | 0.93485 | 3.2516 | 0.56904
12 | 4 | 24 | 114 | 0.48 | 93 | 1 | 42 | 1563.32 | 380 | 384.75 | 21 | 37.8684 | 9.3198 | 1.0174 | 9.2048 | 0.50868
13 | 4 | 24 | 216 | 1.42 | 134 | 1 | 43 | 1292 | 270 | 384.75 | 26 | 30.257 | 9.0104 | 1.007 | 6.3231 | 0.60889
14 | 4 | 24 | 0 | 0 | 0 | 0 | 46 | 1543.94 | 280 | 324.9 | 22 | 37.5506 | 7.902 | 1.1188 | 6.81 | 0.53507
15 | 5 | 24 | 134 | 0.2 | 146 | 1 | 48 | 1466.42 | 280 | 384.75 | 18 | 34.6804 | 9.0992 | 1.1352 | 6.6219 | 0.42569
16 | 5 | 24 | 130 | 0.84 | 149 | 1 | 49 | 1950.92 | 280 | 513 | 15 | 38.2853 | 10.0672 | 0.96159 | 5.4948 | 0.29436
17 | 6 | 24 | 175 | 0.72 | 123 | 1 | 50 | 1925.08 | 260 | 495.9 | 39 | 38.0272 | 9.7958 | 0.98768 | 5.1359 | 0.77039
18 | 4 | 24 | 139 | 0.48 | 108 | 1 | 49 | 1815.26 | 200 | 470.25 | 28 | 39.0066 | 10.1048 | 1.0529 | 4.2976 | 0.60167
19 | 4 | 24 | 0 | 0 | 0 | 0 | 42 | 1576.24 | 280 | 410.4 | 16 | 37.7995 | 9.8417 | 1.0072 | 6.7146 | 0.38369
20 | 4 | 24 | 116 | 0.48 | 122 | 1 | 45 | 1582.7 | 260 | 384.75 | 20 | 37.4304 | 9.0992 | 1.0642 | 6.1489 | 0.47299
21 | 4 | 24 | 0 | 0 | 0 | 0 | 45 | 1550.4 | 240 | 410.4 | 13 | 37.4797 | 9.9211 | 1.0878 | 5.8018 | 0.31426
22 | 4 | 24 | 117 | 0.47 | 93 | 1 | 45 | 1595.62 | 180 | 384.75 | 33 | 37.736 | 9.0992 | 1.0642 | 4.2569 | 0.78044
23 | 4 | 24 | 156 | 6 | 125 | 1 | 45 | 1563.32 | 290 | 367.65 | 17 | 36.9721 | 8.6948 | 1.0642 | 6.8584 | 0.40205
24 | 4 | 24 | 0 | 0 | 0 | 0 | 45 | 1576.24 | 250 | 410.4 | 46 | 37.0584 | 9.6488 | 1.058 | 5.8777 | 1.0815
25 | 5 | 24 | 131 | 0.96 | 115 | 1 | 47 | 1692.52 | 240 | 427.5 | 1 | 37.5815 | 9.4924 | 1.0436 | 5.3291 | 0.022204
26 | 4 | 24 | 0 | 0 | 0 | 0 | 47 | 1724.82 | 260 | 410.4 | 36 | 38.2987 | 9.1127 | 1.0436 | 5.7732 | 0.79936
27 | 4 | 24 | 129 | 3.22 | 299 | 2 | 45 | 1563.32 | 220 | 384.75 | 27 | 37.4897 | 9.2266 | 1.0791 | 5.2758 | 0.64748
28 | 4 | 24 | 119 | 0.48 | 131 | 1 | 45 | 1569.78 | 220 | 410.4 | 17 | 37.72 | 9.8614 | 1.0813 | 5.2864 | 0.40849
29 | 4 | 24 | 0 | 0 | 0 | 0 | 45 | 1576.24 | 220 | 384.75 | 28 | 38.1044 | 9.301 | 1.0878 | 5.3183 | 0.67688
30 | 4 | 24 | 112 | 0.48 | 114 | 1 | 45 | 1543.94 | 410 | 384.75 | 16 | 37.3235 | 9.301 | 1.0878 | 9.9114 | 0.38679
31 | 3 | 24 | 100 | 0.48 | 86 | 1 | 41 | 1408.28 | 240 | 367.65 | 25 | 37.4409 | 9.7744 | 1.09 | 6.3807 | 0.66466
TOTAL |  | 744 |  |  | 2831 | 23 | 1447 | 52177.42 | 8740 | 13184.1 | 667
AVG | 4.1935 |  | 89.6452 | 0.84871 | 91.3226 | 0.74194 | 46.6774 | 1827.0055 | 281.9355 | 462.4773 | 22.2333 | 37.2568 | 9.4888 | 1.0445 | 6.3268 | 0.50132
MIN | 3 |  | 0 | 0 | 0 | 0 | 41 | 1576.24 | 140 | 367.65 | 0 | 30.257 | 7.902 | 0.93485 | 2.4869 | 0
MAX | 6 |  | 216 | 6 | 299 | 2 | 59 | 2164.1 | 500 | 624.15 | 46 | 39.0066 | 13.199 | 1.1352 | 10.5736 | 1.0815

## Monthly Chemical Report
Month, Year: |  | December/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #REF!
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 5.41 | 470.58 | 9.3072 | 50.3521 | 3410.88 | 59.5801 | 322.3282 | 340 | 22.5933 | 122.23 | 384.75 | 51.9164 | 280.8675 | [9 empty] | 27 | 10.4531 | 56.5515 | 178.53 | 153.8501 | 1010.8592
2 | 4.96 | 439.89 | 9.4896 | 47.0682 | 3281.68 | 62.5239 | 310.1188 | 220 | 15.9456 | 79.09 | 367.65 | 54.1098 | 268.3845 | [9 empty] | 0 | 0 | 0 | 163.68 | 142.0688 | 868.3415
3 | 5.25 | 439.89 | 8.9654 | 47.0682 | 3152.48 | 56.7446 | 297.9094 | 340 | 23.2819 | 122.23 | 453.15 | 63.0094 | 330.7995 | [9 empty] | 33 | 13.1654 | 69.1185 | 173.25 | 165.1668 | 1040.3756
4 | 6.75 | 583.11 | 9.2434 | 62.3928 | 4328.2 | 60.5948 | 409.0149 | 140 | 7.4563 | 50.33 | 538.65 | 58.254 | 393.2145 | [9 empty] | 15 | 4.6544 | 31.4175 | 222.75 | 140.2029 | 1169.1197
5 | 5.67 | 491.04 | 9.2665 | 52.5413 | 3643.44 | 60.724 | 344.3051 | 500 | 31.7019 | 179.75 | 624.15 | 80.3579 | 455.6295 | [9 empty] | 10 | 3.694 | 20.945 | 187.11 | 185.7444 | 1240.2809
6 | 5.03 | 439.89 | 9.3575 | 47.0682 | 3178.32 | 59.712 | 300.3512 | 280 | 20.0119 | 100.66 | 427.5 | 62.0427 | 312.075 | [9 empty] | 20 | 8.328 | 41.89 | 165.99 | 159.4522 | 968.0345
7 | 5.82 | 552.42 | 10.1562 | 59.1089 | 3643.44 | 59.1589 | 344.3051 | 360 | 22.2371 | 129.42 | 470.25 | 58.9832 | 343.2825 | [9 empty] | 5 | 1.7994 | 10.4725 | 192.06 | 152.3349 | 1078.649
8 | 6.38 | 603.57 | 10.1226 | 64.582 | 4160.24 | 61.6211 | 393.1427 | 360 | 20.2853 | 129.42 | 470.25 | 53.806 | 343.2825 | [9 empty] | 25 | 8.2073 | 52.3625 | 210.54 | 154.0423 | 1193.3297
9 | 5.57 | 470.58 | 9.0399 | 50.3521 | 3540.08 | 60.0606 | 334.5376 | 300 | 19.3627 | 107.85 | 427.5 | 56.0278 | 312.075 | [9 empty] | 30 | 11.281 | 62.835 | 183.81 | 155.7719 | 1051.4596
10 | 6.35 | 542.19 | 9.1361 | 58.0143 | 4069.8 | 60.5663 | 384.5961 | 480 | 27.1748 | 172.56 | 513 | 58.9748 | 374.49 | [9 empty] | 35 | 11.5445 | 73.3075 | 209.55 | 167.3965 | 1272.5179
11 | 5.9 | 470.58 | 8.5342 | 50.3521 | 3785.56 | 60.6331 | 357.7354 | 160 | 9.7492 | 57.52 | 410.4 | 50.7783 | 299.592 | [9 empty] | 28 | 9.94 | 58.646 | 194.7 | 139.6348 | 1018.5455
12 | 4.95 | 429.66 | 9.2876 | 45.9736 | 3126.64 | 59.6904 | 295.4675 | 380 | 27.598 | 136.61 | 384.75 | 56.7409 | 280.8675 | [9 empty] | 21 | 8.8858 | 43.9845 | 163.35 | 162.2026 | 966.2531
13 | 5.12 | 439.89 | 9.193 | 47.0682 | 2584 | 47.693 | 244.188 | 270 | 18.958 | 97.065 | 384.75 | 54.8569 | 280.8675 | [9 empty] | 26 | 10.6361 | 54.457 | 168.96 | 141.3371 | 892.6057
14 | 4.93 | 470.58 | 10.2134 | 50.3521 | 3087.88 | 59.1896 | 291.8047 | 280 | 20.4178 | 100.66 | 324.9 | 48.1089 | 237.177 | [9 empty] | 22 | 9.3467 | 46.079 | 162.69 | 147.2764 | 888.7627
15 | 5.07 | 491.04 | 10.3632 | 52.5413 | 2932.84 | 54.6654 | 277.1534 | 280 | 19.854 | 100.66 | 384.75 | 55.3979 | 280.8675 | [9 empty] | 18 | 7.4361 | 37.701 | 167.31 | 147.7166 | 916.2332
16 | 6.11 | 501.27 | 8.7784 | 53.6359 | 3901.84 | 60.3476 | 368.7239 | 280 | 16.4746 | 100.66 | 513 | 61.2913 | 374.49 | [9 empty] | 15 | 5.142 | 31.4175 | 201.63 | 152.0339 | 1130.5573
17 | 6.07 | 511.5 | 9.0166 | 54.7305 | 3850.16 | 59.9407 | 363.8401 | 260 | 15.3987 | 93.47 | 495.9 | 59.6387 | 362.007 | [9 empty] | 39 | 13.4572 | 81.6855 | 200.31 | 157.4519 | 1156.0431
18 | 5.58 | 501.27 | 9.6122 | 53.6359 | 3630.52 | 61.4846 | 343.0841 | 200 | 12.8853 | 71.9 | 470.25 | 61.5202 | 343.2825 | [9 empty] | 28 | 10.51 | 58.646 | 184.14 | 156.0123 | 1054.6885
19 | 5 | 429.66 | 9.1947 | 45.9736 | 3152.48 | 59.5819 | 297.9094 | 280 | 20.132 | 100.66 | 410.4 | 59.9184 | 299.592 | [9 empty] | 16 | 6.7024 | 33.512 | 165 | 155.5294 | 942.647
20 | 5.07 | 460.35 | 9.7155 | 49.2574 | 3165.4 | 59.0001 | 299.1303 | 260 | 18.4359 | 93.47 | 384.75 | 55.3979 | 280.8675 | [9 empty] | 20 | 8.2623 | 41.89 | 167.31 | 150.8117 | 931.9252
21 | 4.96 | 460.35 | 9.9309 | 49.2574 | 3100.8 | 59.0777 | 293.0256 | 240 | 17.3952 | 86.28 | 410.4 | 60.4016 | 299.592 | [9 empty] | 13 | 5.4896 | 27.2285 | 163.68 | 152.2951 | 919.0636
22 | 5.07 | 460.35 | 9.7155 | 49.2574 | 3191.24 | 59.4817 | 301.5722 | 180 | 12.7633 | 64.71 | 384.75 | 55.3979 | 280.8675 | [9 empty] | 33 | 13.6328 | 69.1185 | 167.31 | 150.9912 | 932.8356
23 | 5.07 | 460.35 | 9.7155 | 49.2574 | 3126.64 | 58.2776 | 295.4675 | 290 | 20.5631 | 104.255 | 367.65 | 52.9358 | 268.3845 | [9 empty] | 17 | 7.023 | 35.6065 | 167.31 | 148.515 | 920.2809
24 | 5.1 | 460.35 | 9.6583 | 49.2574 | 3152.48 | 58.4136 | 297.9094 | 250 | 17.6225 | 89.875 | 410.4 | 58.7435 | 299.592 | [9 empty] | 46 | 18.8916 | 96.347 | 168.3 | 163.3296 | 1001.2808
25 | 5.4 | 480.81 | 9.5272 | 51.4467 | 3385.04 | 59.2382 | 319.8863 | 240 | 15.9778 | 86.28 | 427.5 | 57.7917 | 312.075 | [9 empty] | 1 | 0.38787 | 2.0945 | 178.2 | 142.9227 | 949.9825
26 | 5.4 | 480.81 | 9.5272 | 51.4467 | 3449.64 | 60.3687 | 325.991 | 260 | 17.3093 | 93.47 | 410.4 | 55.48 | 299.592 | [9 empty] | 36 | 13.9633 | 75.402 | 178.2 | 156.6485 | 1024.1016
27 | 5 | 460.35 | 9.8515 | 49.2574 | 3126.64 | 59.0935 | 295.4675 | 220 | 15.818 | 79.09 | 384.75 | 56.1735 | 280.8675 | [9 empty] | 27 | 11.3103 | 56.5515 | 165 | 152.2468 | 926.2339
28 | 4.99 | 460.35 | 9.8712 | 49.2574 | 3139.56 | 59.4566 | 296.6884 | 220 | 15.8497 | 79.09 | 410.4 | 60.0385 | 299.592 | [9 empty] | 17 | 7.1356 | 35.6065 | 164.67 | 152.3516 | 924.9044
29 | 4.96 | 460.35 | 9.9309 | 49.2574 | 3152.48 | 60.0624 | 297.9094 | 220 | 15.9456 | 79.09 | 384.75 | 56.6265 | 280.8675 | [9 empty] | 28 | 11.8238 | 58.646 | 163.68 | 154.3892 | 929.4503
30 | 4.96 | 460.35 | 9.9309 | 49.2574 | 3087.88 | 58.8316 | 291.8047 | 410 | 29.7167 | 147.395 | 384.75 | 56.6265 | 280.8675 | [9 empty] | 16 | 6.7565 | 33.512 | 163.68 | 161.8622 | 966.5166
31 | 4.51 | 419.43 | 9.951 | 44.879 | 2816.56 | 59.0166 | 266.1649 | 240 | 19.1308 | 86.28 | 367.65 | 59.5088 | 268.3845 | [9 empty] | 25 | 11.6103 | 52.3625 | 148.83 | 159.2175 | 866.9009
Total | 166.41 |  |  | 1583.9007 |  |  | 9861.5324 |  |  | 3142.03 |  |  | 9624.393 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 1449.394 | 5491.53 | 4780.8069 | 31152.78
Avg. | 5.3681 | 477.51 | 9.5356 | 51.0936 | 3366.2852 | 59.1881 | 318.1139 | 281.9355 | 18.9692 | 101.3558 | 425.2935 | 57.7695 | 310.4643 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 22.3226 | 8.7571 | 46.7546 | 177.1461 | 187.205 | 1004.9284
Max | 6.75 | 603.57 | 10.3632 | 64.582 | 4328.2 | 62.5239 | 409.0149 | 500 | 31.7019 | 179.75 | 624.15 | 80.3579 | 455.6295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 18.8916 | 96.347 | 222.75 | 185.7444 | 1272.5179
Min. | 4.51 | 419.43 | 8.5342 | 44.879 | 2584 | 47.693 | 244.188 | 140 | 7.4563 | 50.33 | 324.9 | 48.1089 | 237.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148.83 | 139.6348 | 866.9009
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 2.0945 | Lime | 33 | Per MGD
|  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract |  | 0.1872 | PerKG

## LAS Meter
Month:
LAS Carrier Water Meter
Prev.
1 | 7921600 | 7921600
2 | 7960970 | 39370
3 | 8000810 | 39840
4 | 8040730 | 39920
5 | 8080480 | 39750
6 | 8120360 | 39880
7 | 8160410 | 40050
8 | 8200040 | 39630
9 | 8239790 | 39750
10 | 8279520 | 39730
11 | 8319380 | 39860
12 | 8358500 | 8358500
13 | 8399250 | 40750
14 | 8437970 | 38720
15 | 8476730 | 38760
16 | 8516730 | 40000
17 | 8556950 | 40220
18 | 8596400 | 39450
19 | 8636050 | 39650
20 | 8675940 | 39890
21 | 8714950 | 39010
22 | 8754670 | 39720
23 | 8794050 | 39380
24 | 8833680 | 39630
25 | 8873420 | 39740
26 | 8913180 | 39760
27 | 8952760 | 39580
28 | 8992000 | 39240
29 | 9031470 | 39470
30 | 9071320 | 39850
31 | 9111380 | 40060
Total |  | 17430760

## Graphs
Chemicals | Amount
LAS | 2021.7447
Fe | 9861.5324
CL2 | 3142.03
Poly | 9624.393
Potassium | 1449.394
Lime | 0
Chemfloc 3315 | 31152.78