## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: February 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 17088.99 |  | 2868037 |  | 34.5528 |  | 26731 |  | 7033443 |  | 13675.22 |  |  |  |  | 4404.63
1 | 17094.45 | 5.46 | 2982826 | 0.11479 | 34.5529 | 0.0001 | 26862 | 0.131 | 7137141 | 0.1037 | 13680.85 | 5.63 | 731.13 | 22382 | 534.73 | 4404.63 | 0
2 | 17098.03 | 3.58 | 3127106 | 0.14428 | 34.553 | 0.0001 | 26983 | 0.121 | 7217690 | 0.080549 | 13684.94 | 4.09 | 731.13 | 22382 | 534.72 | 4404.63 | 0
3 | 17103.16 | 5.13 | 3127106 | 0 | 34.553 | 0 | 26983 | 0 | 7311557 | 0.093867 | 13689.98 | 5.04 | 731.12 | 22367 | 534.7 | 4404.63 | 0
4 | 17108.62 | 5.46 | 3395406 | 0.2683 | 34.6409 | 0.0879 | 27083 | 0.1 | 7417254 | 0.1057 | 13695.44 | 5.46 | 731.12 | 22367 | 534.73 | 4404.63 | 0
5 | 17112.36 | 3.74 | 3497749 | 0.10234 | 34.641 | 0.0001 | 27279 | 0.196 | 7503985 | 0.086731 | 13699.61 | 4.17 | 731.05 | 22263 | 534.73 | 4404.63 | 0
6 | 17116.92 | 4.56 | 3572607 | 0.074858 | 34.6411 | 0.0001 | 27279 | 0 | 7599239 | 0.095254 | 13704.17 | 4.56 | 731.08 | 22308 | 534.7 | 4404.63 | 0
7 | 17121.96 | 5.04 | 3572607 | 0 | 34.6412 | 0.0001 | 27279 | 0 | 7700391 | 0.10115 | 13709.21 | 5.04 | 731.08 | 22308 | 534.68 | 4404.63 | 0
8 | 17127.03 | 5.07 | 3761057 | 0.18845 | 34.715 | 0.0738 | 27361 | 0.082 | 7803776 | 0.10339 | 13714.22 | 5.01 | 731.07 | 22293 | 534.67 | 4404.63 | 0
9 | 17131.11 | 4.08 | 3761058 | 1e-06 | 34.715 | 0 | 27471 | 0.11 | 7892692 | 0.088916 | 13718.41 | 4.19 | 731.06 | 22278 | 534.66 | 4404.63 | 0
10 | 17135.86 | 4.75 | 4025477 | 0.26442 | 34.7151 | 0.0001 | 27471 | 0 | 7985211 | 0.092519 | 13723.23 | 4.82 | 731.07 | 22293 | 534.73 | 4404.63 | 0
11 | 17140.44 | 4.58 | 4124260 | 0.098783 | 34.7775 | 0.0624 | 27573 | 0.102 | 8074888 | 0.089677 | 13728.06 | 4.83 | 731.09 | 22322 | 534.89 | 4404.63 | 0
12 | 17145.12 | 4.68 | 4378620 | 0.25436 | 34.7775 | 0 | 27780 | 0.207 | 8165351 | 0.090463 | 13732.76 | 4.7 | 731.39 | 22772 | 535.67 | 4404.63 | 0
13 | 17150.17 | 5.05 | 4378620 | 0 | 34.7776 | 0.0001 | 27780 | 0 | 8266187 | 0.10084 | 13737.53 | 4.77 | 732.01 | 23710 | 538.2 | 4404.63 | 0
14 | 17153.31 | 3.14 | 4449371 | 0.070751 | 34.7777 | 0.0001 | 27780 | 0 | 8348610 | 0.082423 | 13741.56 | 4.03 | 732.09 | 23847 | 538.35 | 4404.63 | 0
15 | 17158.36 | 5.05 | 4539264 | 0.089893 | 34.8428 | 0.0651 | 27780 | 0 | 8440375 | 0.091765 | 13746.11 | 4.55 | 732.1 | 23847 | 538.35 | 4404.63 | 0
16 | 17162.85 | 4.49 | 4626691 | 0.087427 | 34.8428 | 0 | 27911 | 0.131 | 8531070 | 0.090695 | 13750.68 | 4.57 |  | 23892 | 538.34 | 4404.63 | 0
17 | 17167.99 | 5.14 | 4813739 | 0.18705 | 34.913 | 0.0702 | 28033 | 0.122 | 8636900 | 0.10583 | 13755.86 | 5.18 | 732.15 | 23923 | 538.29 | 4404.63 | 0
18 | 17172.29 | 4.3 | 4940715 | 0.12698 | 34.913 | 0 | 28107 | 0.074 | 8729014 | 0.092114 | 13760.31 | 4.45 | 732.16 | 23938 | 538.29 | 4404.63 | 0
19 | 17177.34 | 5.05 | 5107197 | 0.16648 | 34.9131 | 0.0001 | 28107 | 0 | 8849320 | 0.12031 | 13765.31 | 5 | 732.26 | 24091 | 538.36 | 4404.63 | 0
20 | 17180.67 | 3.33 | 5107197 | 0 | 34.9781 | 0.065 | 28107 | 0 | 8913535 | 0.064215 | 13769.08 | 3.77 | 732.55 | 24504 | 538.73 | 4404.79 | 0.16
21 | 17185.69 | 5.02 | 5171539 | 0.064342 | 34.9782 | 0.0001 | 28107 | 0 | 9013515 | 0.09998 | 13773.95 | 4.87 | 732.98 | 25199 | 539.26 | 4404.79 | 0
22 | 17190.92 | 5.23 | 5411789 | 0.24025 | 34.9782 | 0 | 28257 | 0.15 | 9116572 | 0.10306 | 13779.34 | 5.39 | 733.03 | 25276 | 538.95 | 4404.79 | 0
23 | 17194.68 | 3.76 | 5487508 | 0.075719 | 34.9783 | 0.0001 | 28404 | 0.147 | 9202441 | 0.085869 | 13783.34 | 4 | 733.07 | 25338 | 538.61 | 4404.79 | 0
24 | 17199.98 | 5.3 | 5734927 | 0.24742 | 35.0238 | 0.0455 | 28550 | 0.146 | 9305215 | 0.10277 | 13788.36 | 5.02 | 733.12 | 25416 | 538.03 | 4404.79 | 0
25 | 17205.13 | 5.15 | 5833780 | 0.098853 | 35.0907 | 0.0669 | 28550 | 0 | 9406321 | 0.10111 | 13793.57 | 5.21 | 733.04 | 25292 | 537.89 | 4404.79 | 0
26 | 17208.36 | 3.23 | 5984535 | 0.15076 | 35.0908 | 0.0001 | 28666 | 0.116 | 9480828 | 0.074507 | 13797.35 | 3.78 | 733.07 | 25338 | 537.87 | 4406.62 | 1.83
27 | 17213.47 | 5.11 | 5984535 | 0 | 35.0909 | 0.0001 | 28763 | 0.097 | 9580723 | 0.099895 | 13802.35 | 5 | 733.14 | 25447 | 537.73 | 4411.65 | 5.03
28 | 17218.6 | 5.13 | 6109159 | 0.12462 | 35.1603 | 0.0694 | 28763 | 0 | 9682825 | 0.1021 | 13807.47 | 5.12 | 733.16 | 24578 | 537.7 | 4416.64 | 4.99
29 | 17222.81 | 4.21 | 6166023 | 0.056864 | 35.1604 | 0.0001 | 28907 | 0.144 | 9773027 | 0.090202 | 13811.75 | 4.28 | 733.16 | 25478 | 537.68 | 4421.63 | 4.99
30
31
Totals | 497597.68 | 133.82 |  | 3.298 |  | 0.6076 |  | 2.176 |  | 2.7396 |  | 136.53 |  |  |  |  | 17
Average | 17158.5407 | 4.6145 |  | 0.11372 |  | 0.020952 |  | 0.075034 |  | 0.094468 |  | 4.7079 | 732.0171 |  | 536.8359 |  | 0.58621
Min |  | 3.14 |  | 0 |  | 0 |  | 0 |  | 0.064215 |  | 3.77 | 731.05 |  | 534.66 |  | 0
Max |  | 5.46 |  | 0.2683 |  | 0.0879 |  | 0.207 |  | 0.12031 |  | 5.63 | 733.16 |  | 539.26 |  | 5.03
Calculated Values
| Raw Water Added To System (MG) |  |  | 130.522 |  |  | Raw to Potable Differential |  |  | -1.0924
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 131.6144 |  |  | Average Raw for Month |  |  | 4.6145
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.51439 |  |  | Peak Raw Flow for Month |  |  | 5.46
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | February/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 48 | 0 | 15.1667 | 5.61 | 1.6717 | 0.061667 | 8.52 | 8.7967 | 3.7342 | 128 | 147.3333 | 82 | 86 | 7
2 | 52 | 0 | 15 | 10.6 | 2.195 | 0.070167 | 8.42 | 8.7367 | 3.665 | 122 | 146.3333 | 89 | 82.6667 | 6.3333
3 | 64 | 0 | 15.5 | 9.23 | 2.246 | 0.069667 | 8.5 | 8.7917 | 3.7075 | 126 | 144 | 88 | 75 | 5.3333
4 | 36 | 0 | 14.6667 | 9.69 | 1.93 | 0.074 | 8.41 | 8.78 | 3.725 | 133 | 137 | 96 | 73 | 4.6667
5 | 35 | 0.1 | 14.3333 | 9.54 | 2.354 | 0.088 | 8.41 | 8.85 | 3.6675 | 131 | 132.6667 | 87 | 71.3333 | 7.3333
6 | 34 | 0 | 14.1667 | 10.2 | 2.38 | 0.089167 | 8.26 | 8.7183 | 3.6375 | 126 | 143.3333 | 92 | 82.6667 | 4
7 | 39 | 0 | 15.8333 | 9.47 | 2.2417 | 0.0645 | 8.35 | 8.78 | 3.7008 | 140 | 142.6667 | 97 | 78.6667 | 5.3333
8 | 61 | 0 | 13.5 | 7.53 | 2.3167 | 0.060667 | 8.34 | 8.775 | 3.6458 | 126 | 143.3333 | 88 | 80.3333 | 4.3333
9 | 57 | 0.1 | 15.5 | 8.7 | 2.2475 | 0.087333 | 8.46 | 8.8267 | 3.4382 | 125 | 140.3333 | 94 | 78.6667 | 6.3333
10 | 40 | 0.3 | 14.5 | 10.5 | 1.9975 | 0.081333 | 8.33 | 8.7417 | 3.6517 | 123 | 143.3333 | 92 | 78.6667 | 4.3333
11 | 43 | 1.5 | 13.8333 | 12.5 | 2.382 | 0.084 | 8.39 | 8.8683 | 3.8675 | 140 | 141.3333 | 90 | 71 | 7.3333
12 | 43 | 2" | 14.8333 | 15.9 | 2.178 | 0.12283 | 8.05 | 8.8183 | 3.8017 | 135 | 140 | 96 | 74.6667 | 6.6667
13 | 34 | .1" | 13.8333 | 12.6 | 1.96 | 0.1045 | 8.38 | 8.8267 | 3.7592 | 126 | 98.0423 | 97 | 79.3333 | 8.6667
14 | 40 | 0 | 13.8333 | 10.7 | 2.1733 | 0.074375 | 8.42 | 8.6717 | 3.6542 | 131 | 146.6667 | 92 | 79.6667 | 3.6667
15 | 54 | 0 | 13.6667 | 9.52 | 2.25 | 0.061833 | 8.46 | 8.8233 | 3.7483 | 126 | 151.6667 | 93 | 84.3333 | 3
16 | 58 | 0 | 13.5 | 11.9 | 2.166 | 0.092333 | 8.41 | 8.8733 | 3.7933 | 123 | 143 | 92 | 77.3333 | 7
17 | 58 | 0 | 14.3333 | 11.1 | 1.8217 | 0.080833 | 8.59 | 8.8283 | 3.7242 | 120 | 145.3333 | 90 | 82 | 3.3333
18 | 58 | 0 | 14.3333 | 11 | 1.952 | 0.114 | 8.5 | 8.8483 | 3.7608 | 130 | 143.3333 | 96 | 74.6667 | 7.6667
19 | 43 | 1.5 | 15 | 9.32 | 2.1533 | 0.10583 | 8.62 | 8.8783 | 3.6117 | 140 | 139.6667 | 100 | 81.6667 | 7.3333
20 | 36 | 0.4 | 15.8333 | 11 | 2.085 | 0.070667 | 8.48 | 8.8 | 3.5708 | 140 | 146.3333 | 95 | 84 | 7.3333
21 | 43 | 0 | 13.8333 | 11 | 1.8267 | 0.085 | 8.49 | 8.7317 | 3.2242 | 135 | 157 | 95 | 87 | 2.6667
22 | 47 | 0 | 13.3333 | 10 | 2.5367 | 0.10983 | 8.47 | 8.855 | 3.7583 | 140 | 149.6667 | 92 | 84.3333 | 5.6667
23 | 61 | .2" | 13.8333 | 12.1 | 2.266 | 0.1155 | 8.59 | 8.85 | 3.8167 | 145 | 144.6667 | 95 | 79 | 7.6667
24 | 46 | 0 | 14.1667 | 13 | 2.2317 | 0.091833 | 8.65 | 8.8583 | 3.8183 | 138 | 147.6667 | 90 | 80.6667 | 5.3333
25 | 45 | 0 | 14.8333 | 13.3 | 2.265 | 0.094667 | 8.57 | 8.86 | 3.6958 | 145 | 145.3333 | 97 | 83.3333 | 6.3333
26 | 39 | 0 | 16.1667 | 14.9 | 1.835 | 0.1435 | 8.63 | 8.84 | 3.5817 | 148 | 154 | 99 | 91 | 3.6667
27 | 43 | 0 | 14 | 10.8 | 2.2867 | 0.11092 | 8.54 | 8.8917 | 3.4517 | 140 | 156.3333 | 98 | 87.3333 | 8.6667
28 | 54 | 0 | 14 | 11.6 | 1.82 | 0.08 | 8.58 | 8.875 | 3.5417 | 131 | 153 | 91 | 84.3333 | 4
29 | 54 | 0 | 15.8333 | 12.1 | 2.024 | 0.12617 | 8.42 | 8.7617 | 3.9 | 140 | 157.3333 | 95 | 95.6667 | 6.6667
30
31
TOTAL |  | 3.9
AVG. | 47.069 | 0.15 | 14.523 | 10.8762 | 2.1308 | 0.090177 | 8.4566 | 8.8123 | 3.6777 | 132.8621 | 144.1624 | 93.0345 | 80.977 | 5.7816
MAX. | 64 | 1.5 | 16.1667 | 15.9 | 2.5367 | 0.1435 | 8.65 | 8.8917 | 3.9 | 148 | 157.3333 | 100 | 95.6667 | 8.6667
MIN. | 34 | 0 | 13.3333 | 5.61 | 1.6717 | 0.060667 | 8.05 | 8.6717 | 3.2242 | 120 | 98.0423 | 82 | 71 | 2.6667

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: February 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 4 | 24 | 118 | 0.48 | 131 | 1 | 35 | 1750.66 | 400 | 384.75 | 46 | 38.4453 | 8.4493 | 0.76862 | 8.7842 | 1.0102
2 | 4 | 18 | 101 | 0.48 | 121 | 1 | 21 | 1169.26 | 330 | 256.5 | 43 | 39.1617 | 8.5909 | 0.70335 | 11.0526 | 1.4402
3 | 3 | 21.75 | 0 | 0 | 0 | 0 | 32 | 1595.62 | 30 | 367.65 | 27 | 37.2946 | 8.5931 | 0.74794 | 0.70119 | 0.63107
4 | 4 | 24 | 144 | 0.51 | 100 | 1 | 34 | 1718.36 | 420 | 367.65 | 40 | 37.736 | 8.0738 | 0.74666 | 9.2234 | 0.87842
5 | 3 | 18 | 132 | 3.18 | 196 | 2 | 24 | 1175.72 | 300 | 282.15 | 43 | 37.6935 | 9.0457 | 0.76944 | 9.618 | 1.3786
6 | 3 | 21.25 | 0 | 0 | 0 | 0 | 23 | 1453.5 | 380 | 299.25 | 30 | 38.2194 | 7.8687 | 0.60478 | 9.992 | 0.78884
7 | 3 | 24 | 0 | 0 | 0 | 0 | 31 | 1744.2 | 180 | 367.65 | 29 | 41.4954 | 8.7466 | 0.73751 | 4.2823 | 0.68992
8 | 3 | 24 | 116 | 0.51 | 82 | 1 | 31 | 1757.12 | 210 | 384.75 | 48 | 41.5554 | 9.0992 | 0.73314 | 4.9664 | 1.1352
9 | 3 | 19 | 113 | 0.72 | 110 | 1 | 27 | 1382.44 | 190 | 282.15 | 31 | 40.6275 | 8.2919 | 0.79348 | 5.5838 | 0.91104
10 | 3 | 19 | 0 | 0 | 0 | 0 | 30 | 1666.68 | 240 | 367.65 | 34 | 42.0719 | 9.2806 | 0.75729 | 6.0583 | 0.85826
11 | 3 | 18 | 115 | 0.96 | 102 | 1 | 28 | 1576.24 | 360 | 299.25 | 45 | 41.2659 | 7.8343 | 0.73304 | 9.4248 | 1.1781
12 | 3 | 22 | 107 | 3.89 | 207 | 2 | 29 | 1647.3 | 80 | 299.25 | 9 | 42.2047 | 7.6669 | 0.75196 | 2.0496 | 0.29
13 | 3 | 24 | 0 | 0 | 0 | 0 | 31 | 1744.2 | 300 | 363.375 | 51 | 41.4132 | 8.6278 | 0.73604 | 7.123 | 1.2109
14 | 3 | 17.5 | 0 | 0 | 0 | 0 | 25 | 1111.12 | 140 | 213.75 | 7 | 42.4292 | 8.1623 | 0.95465 | 5.346 | 0.2673
15 | 3 | 20 | 0 | 0 | 0 | 0 | 31 | 1744.2 | 280 | 320.625 | 43 | 41.4132 | 7.6127 | 0.73604 | 6.6481 | 1.021
16 | 3 | 20 | 97 | 0.48 | 131 | 1 | 28 | 1569.78 | 190 | 324.9 | 44 | 41.9205 | 8.6764 | 0.74773 | 5.0739 | 1.175
17 | 3 | 24 | 108 | 0.55 | 122 | 1 | 31 | 1782.96 | 250 | 384.75 | 45 | 41.5923 | 8.9753 | 0.72316 | 5.8319 | 1.0497
18 | 3 | 19 | 109 | 0.51 | 74 | 1 | 26 | 1447.04 | 350 | 299.25 | 40 | 40.3502 | 8.3445 | 0.725 | 9.7596 | 1.1154
19 | 3 | 24 | 0 | 0 | 0 | 0 | 33 | 1550.4 | 270 | 342 | 37 | 36.8117 | 8.1202 | 0.78353 | 6.4107 | 0.87851
20 | 3 | 15.5 | 0 | 0 | 0 | 0 | 24 | 1033.6 | 180 | 239.4 | 31 | 37.2171 | 8.6201 | 0.86417 | 6.4813 | 1.1162
21 | 3 | 24 | 0 | 0 | 0 | 0 | 39 | 1563.32 | 190 | 367.65 | 35 | 37.3403 | 8.7814 | 0.93153 | 4.5382 | 0.83598
22 | 3 | 24 | 103 | 0.96 | 150 | 1 | 38 | 1582.7 | 290 | 367.65 | 31 | 36.2853 | 8.4288 | 0.8712 | 6.6486 | 0.71071
23 | 3 | 18.5 | 118 | 0.97 | 147 | 1 | 29 | 1156.34 | 110 | 282.15 | 37 | 36.875 | 8.9976 | 0.92479 | 3.5078 | 1.1799
24 | 3 | 24 | 117 | 0.48 | 146 | 1 | 38 | 1608.54 | 290 | 384.75 | 44 | 36.3907 | 8.7044 | 0.85969 | 6.5608 | 0.99543
25 | 3 | 24 | 0 | 0 | 0 | 0 | 38 | 1569.78 | 300 | 367.65 | 36 | 36.5482 | 8.5598 | 0.88473 | 6.9847 | 0.83816
26 | 3 | 15 | 106 | 8 | 116 | 1 | 24 | 1001.3 | 190 | 239.4 | 30 | 37.1703 | 8.887 | 0.89093 | 7.0532 | 1.1137
27 | 3 | 24 | 99 | 0.48 | 97 | 1 | 41 | 1569.78 | 300 | 367.65 | 31 | 36.8343 | 8.6268 | 0.96205 | 7.0394 | 0.7274
28 | 3 | 24 | 0 | 0 | 0 | 0 | 43 | 1576.24 | 570 | 342 | 33 | 36.8416 | 7.9936 | 1.005 | 13.3227 | 0.77131
29 | 3 | 18 | 119 | 0.48 | 144 | 1 | 32 | 1292 | 220 | 299.25 | 25 | 36.7972 | 8.5229 | 0.91138 | 6.2658 | 0.71202
30
31
TOTAL |  | 612.5 |  |  | 2176 | 19 | 896 | 43540.4 | 7540 | 9464.85 | 1025
AVG | 3.1034 |  | 66.2759 | 0.81517 | 75.0345 | 0.65517 | 30.8966 | 1544.5273 | 260 | 332.6727 | 35.3448 | 38.8264 | 8.4891 | 0.80548 | 6.7701 | 0.92788
MIN | 3 |  | 0 | 0 | 0 | 0 | 21 | 1169.26 | 30 | 256.5 | 7 | 36.2853 | 7.6127 | 0.60478 | 0.70119 | 0.2673
MAX | 4 |  | 144 | 8 | 207 | 2 | 43 | 1757.12 | 570 | 384.75 | 51 | 42.4292 | 9.2806 | 1.005 | 13.3227 | 1.4402

## Monthly Chemical Report
Month, Year: |  | February/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #REF!
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 5.46 | 358.05 | 7.0167 | 38.3113 | 3501.32 | 60.5998 | 330.8747 | 400 | 26.337 | 143.8 | 384.75 | 51.4409 | 280.8675 | [9 empty] | 46 | 17.646 | 96.347 | 180.18 | 163.0404 | 1070.3806
2 | 3.58 | 214.83 | 6.4209 | 22.9868 | 2338.52 | 61.7291 | 220.9901 | 330 | 33.1383 | 118.635 | 256.5 | 52.3031 | 187.245 | [9 empty] | 43 | 25.1574 | 90.0635 | 118.14 | 178.7487 | 758.0604
3 | 5.13 | 327.36 | 6.828 | 35.0275 | 3191.24 | 58.786 | 301.5722 | 30 | 2.1023 | 10.785 | 367.65 | 52.3167 | 268.3845 | [9 empty] | 27 | 11.0237 | 56.5515 | 169.29 | 131.0567 | 841.6107
4 | 5.46 | 347.82 | 6.8163 | 37.2167 | 3436.72 | 59.4817 | 324.77 | 420 | 27.6538 | 150.99 | 367.65 | 49.1547 | 268.3845 | [9 empty] | 40 | 15.3443 | 83.78 | 180.18 | 158.4508 | 1045.3213
5 | 3.74 | 245.52 | 7.0242 | 26.2706 | 2351.44 | 59.4147 | 222.2111 | 300 | 28.8369 | 107.85 | 282.15 | 55.0721 | 205.9695 | [9 empty] | 43 | 24.0811 | 90.0635 | 123.42 | 174.4291 | 775.7847
6 | 4.56 | 235.29 | 5.5211 | 25.176 | 2907 | 60.2438 | 274.7115 | 380 | 29.9583 | 136.61 | 299.25 | 47.9063 | 218.4525 | [9 empty] | 30 | 13.7796 | 62.835 | 150.48 | 157.409 | 868.265
7 | 5.04 | 317.13 | 6.7327 | 33.9329 | 3488.4 | 65.4075 | 329.6538 | 180 | 12.8393 | 64.71 | 367.65 | 53.2509 | 268.3845 | [9 empty] | 29 | 12.0517 | 60.7405 | 166.32 | 150.2821 | 923.7417
8 | 5.07 | 317.13 | 6.6929 | 33.9329 | 3514.24 | 65.5021 | 332.0957 | 210 | 14.8905 | 75.495 | 384.75 | 55.3979 | 280.8675 | [9 empty] | 48 | 19.8296 | 100.536 | 167.31 | 162.313 | 990.2371
9 | 4.08 | 276.21 | 7.2437 | 29.5545 | 2764.88 | 64.0395 | 261.2812 | 190 | 16.7414 | 68.305 | 282.15 | 50.4827 | 205.9695 | [9 empty] | 31 | 15.9141 | 64.9295 | 134.64 | 154.4215 | 764.6796
10 | 4.75 | 306.9 | 6.9133 | 32.8383 | 3333.36 | 66.3163 | 315.0025 | 240 | 18.1642 | 86.28 | 367.65 | 56.502 | 268.3845 | [9 empty] | 34 | 14.9922 | 71.213 | 156.75 | 162.8881 | 930.4683
11 | 4.58 | 286.44 | 6.6919 | 30.6491 | 3152.48 | 65.0457 | 297.9094 | 360 | 28.2576 | 129.42 | 299.25 | 47.6971 | 218.4525 | [9 empty] | 45 | 20.5791 | 94.2525 | 151.14 | 168.2715 | 921.8234
12 | 4.68 | 296.67 | 6.7828 | 31.7437 | 3294.6 | 66.5256 | 311.3397 | 80 | 6.1453 | 28.76 | 299.25 | 46.6779 | 218.4525 | [9 empty] | 9 | 4.0279 | 18.8505 | 154.44 | 130.1595 | 763.5864
13 | 5.05 | 317.13 | 6.7194 | 33.9329 | 3488.4 | 65.278 | 329.6538 | 300 | 21.3564 | 107.85 | 363.375 | 52.5275 | 265.2638 | [9 empty] | 51 | 21.1524 | 106.8195 | 166.65 | 167.0337 | 1010.17
14 | 3.14 | 255.75 | 8.715 | 27.3652 | 2222.24 | 66.8795 | 210.0017 | 140 | 16.0287 | 50.33 | 213.75 | 49.6935 | 156.0375 | [9 empty] | 7 | 4.6693 | 14.6615 | 103.62 | 145.986 | 562.0159
15 | 5.05 | 317.13 | 6.7194 | 33.9329 | 3488.4 | 65.278 | 329.6538 | 280 | 19.9327 | 100.66 | 320.625 | 46.3478 | 234.0563 | [9 empty] | 43 | 17.8344 | 90.0635 | 166.65 | 156.1122 | 955.0165
16 | 4.49 | 286.44 | 6.8261 | 30.6491 | 3139.56 | 66.0776 | 296.6884 | 190 | 15.2127 | 68.305 | 324.9 | 52.8234 | 237.177 | [9 empty] | 44 | 20.5252 | 92.158 | 148.17 | 161.4649 | 873.1475
17 | 5.14 | 317.13 | 6.6017 | 33.9329 | 3565.92 | 65.5602 | 336.9794 | 250 | 17.4854 | 89.875 | 384.75 | 54.6435 | 280.8675 | [9 empty] | 45 | 18.3371 | 94.2525 | 169.62 | 162.6279 | 1005.5274
18 | 4.3 | 265.98 | 6.6186 | 28.4599 | 2894.08 | 63.6025 | 273.4906 | 350 | 29.2616 | 125.825 | 299.25 | 50.8029 | 218.4525 | [9 empty] | 40 | 19.4837 | 83.78 | 141.9 | 169.7693 | 871.9079
19 | 5.05 | 337.59 | 7.1529 | 36.1221 | 3100.8 | 58.0249 | 293.0256 | 270 | 19.2208 | 97.065 | 342 | 49.4376 | 249.66 | [9 empty] | 37 | 15.3458 | 77.4965 | 166.65 | 149.182 | 920.0192
20 | 3.33 | 245.52 | 7.8891 | 26.2706 | 2067.2 | 58.6638 | 195.3504 | 180 | 19.4324 | 64.71 | 239.4 | 52.4811 | 174.762 | [9 empty] | 31 | 19.4983 | 64.9295 | 109.89 | 157.9647 | 635.9125
21 | 5.02 | 398.97 | 8.5039 | 42.6898 | 3126.64 | 58.8581 | 295.4675 | 190 | 13.6066 | 68.305 | 367.65 | 53.463 | 268.3845 | [9 empty] | 35 | 14.6031 | 73.3075 | 165.66 | 149.0347 | 913.8143
22 | 5.23 | 388.74 | 7.9532 | 41.5952 | 3165.4 | 57.1951 | 299.1303 | 290 | 19.934 | 104.255 | 367.65 | 51.3163 | 268.3845 | [9 empty] | 31 | 12.4148 | 64.9295 | 172.59 | 148.8135 | 950.8845
23 | 3.76 | 296.67 | 8.4425 | 31.7437 | 2312.68 | 58.1245 | 218.5483 | 110 | 10.5173 | 39.545 | 282.15 | 54.7791 | 205.9695 | [9 empty] | 37 | 20.6108 | 77.4965 | 124.08 | 152.4742 | 697.383
24 | 5.3 | 388.74 | 7.8481 | 41.5952 | 3217.08 | 57.3611 | 304.0141 | 290 | 19.6708 | 104.255 | 384.75 | 52.9939 | 280.8675 | [9 empty] | 44 | 17.3883 | 92.158 | 174.9 | 155.2622 | 997.7897
25 | 5.15 | 388.74 | 8.0767 | 41.5952 | 3139.56 | 57.6094 | 296.6884 | 300 | 20.9417 | 107.85 | 367.65 | 52.1135 | 268.3845 | [9 empty] | 36 | 14.6412 | 75.402 | 169.95 | 153.3825 | 959.8701
26 | 3.23 | 245.52 | 8.1333 | 26.2706 | 2002.6 | 58.59 | 189.2457 | 190 | 21.1471 | 68.305 | 239.4 | 54.1059 | 174.762 | [9 empty] | 30 | 19.4536 | 62.835 | 106.59 | 161.4298 | 628.0083
27 | 5.11 | 419.43 | 8.7826 | 44.879 | 3139.56 | 58.0604 | 296.6884 | 300 | 21.1057 | 107.85 | 367.65 | 52.5214 | 268.3845 | [9 empty] | 31 | 12.7064 | 64.9295 | 168.63 | 153.1764 | 951.3614
28 | 5.13 | 439.89 | 9.1751 | 47.0682 | 3152.48 | 58.072 | 297.9094 | 570 | 39.9444 | 204.915 | 342 | 48.6667 | 249.66 | [9 empty] | 33 | 13.4734 | 69.1185 | 169.29 | 169.3316 | 1037.9611
29 | 4.21 | 327.36 | 8.3201 | 35.0275 | 2584 | 58.0019 | 244.188 | 220 | 18.7862 | 79.09 | 299.25 | 51.889 | 218.4525 | [9 empty] | 25 | 12.4376 | 52.3625 | 138.93 | 149.4348 | 768.0505
30
31
Total | 133.82 |  |  | 980.7706 |  |  | 8229.1356 |  |  | 2710.63 |  |  | 6909.3405 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 2146.8625 | 4416.06 | 4553.9507 | 25392.7992
Avg. | 4.6145 | 316.0717 | 7.3504 | 33.8197 | 3002.7862 | 61.5286 | 283.7633 | 260 | 20.2983 | 93.47 | 326.3741 | 51.683 | 238.2531 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 35.3448 | 16.1725 | 74.0297 | 152.2779 | 189.7534 | 875.6138
Max | 5.46 | 439.89 | 9.1751 | 47.0682 | 3565.92 | 66.8795 | 336.9794 | 570 | 39.9444 | 204.915 | 384.75 | 56.502 | 280.8675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 25.1574 | 106.8195 | 180.18 | 178.7487 | 1070.3806
Min. | 3.14 | 214.83 | 5.5211 | 22.9868 | 2002.6 | 57.1951 | 189.2457 | 30 | 2.1023 | 10.785 | 213.75 | 46.3478 | 156.0375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4.0279 | 14.6615 | 103.62 | 130.1595 | 562.0159
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 2.0945 | Lime | 33 | Per MGD
|  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract |  | 0.18975 | PerKG

## LAS Meter
LAS carrier water meter
0 | 7183970
1 | 7224930 | 40960
2 | 7251770 | 26840
3 | 7288450 | 36680
4 | 7329690 | 41240
5 | 7360870 | 31180
6 | 7396580 | 35710
7 | 7437060 | 40480
8 | 7477780 | 40720
9 | 7509380 | 31600
10 | 7541840 | 32460
11 | 7573270 | 31430
12 | 7606500 | 33230
13 | 7647070 | 40570
14 | 7670330 | 23260
15 | 7704180 | 33850
16 | 7737500 | 33320
17 | 7778470 | 40970
18 | 7812120 | 33650
19 | 7851830 | 39710
20 | 7878540 | 26710
21 | 7918410 | 39870
22 | 7959210 | 40800
23 | 7988830 | 29620
24 | 8029770 | 40940
25 | 8070480 | 40710
26 | 8095640 | 25160
27 | 8135620 | 39980
28 | 8175860 | 40240
29 | 8209040 | 33180
30
31
Total |  | 1025070

## Graphs
Chemicals | Amount
LAS | #REF!
Fe | 8229.1356
CL2 | 2710.63
Poly | 6909.3405
Potassium | 2146.8625
Lime | 0
Chemfloc 3315 | 25392.7992