## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: January 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 16935.63 |  | 8926268 |  | 33.7134 |  | 24237 |  | 4078045 |  | 13519.75 |  |  |  |  | 4333.02
1 | 16940.57 | 4.94 | 8996750 | 0.070482 | 33.7135 | 0.0001 | 24435 | 0.198 | 4180605 | 0.10256 | 13524.64 | 4.89 | 730.42 | 21327 | 534.59 | 4337.99 | 4.97
2 | 16945.69 | 5.12 | 9254676 | 0.25793 | 33.7972 | 0.0837 | 24527 | 0.092 | 4281703 | 0.1011 | 13529.65 | 5.01 | 730.41 | 21312 | 534.57 | 4343.04 | 5.05
3 | 16948.93 | 3.24 | 9264466 | 0.00979 | 33.7973 | 0.0001 | 24527 | 0 | 4354080 | 0.072377 | 13533.63 | 3.98 | 730.42 | 21327 | 534.57 | 4348.05 | 5.01
4 | 16955.01 | 6.08 | 9264466 | 0 | 33.7974 | 0.0001 | 24527 | 0 | 4451064 | 0.096984 | 13539.36 | 5.73 | 730.41 | 21312 | 534.55 | 4349.03 | 0.98
5 | 16959.44 | 4.43 | 9363414 | 0.098948 | 33.8267 | 0.0293 | 24649 | 0.122 | 4545222 | 0.094158 | 13543.82 | 4.46 | 730.4 | 21298 | 534.54 | 4349.03 | 0
6 | 16964.02 | 4.58 | 9716924 | 0.35351 | 33.8739 | 0.0472 | 24649 | 0 | 4640903 | 0.095681 | 13548.7 | 4.88 | 730.37 | 21253 | 534.54 | 4349.1 | 0.07
7 | 16970.13 | 6.11 | 9716924 | 0 | 33.8739 | 0 | 24782 | 0.133 | 4743970 | 0.10307 | 13554.32 | 5.62 | 730.36 | 21239 | 534.52 | 4349.1 | 0
8 | 16974.37 | 4.24 | 9984238 | 0.26731 | 33.874 | 0.0001 | 24894 | 0.112 | 4822092 | 0.078122 | 13558.74 | 4.42 | 730.35 | 21224 | 534.51 | 4349.72 | 0.62
9 | 16979.28 | 4.91 | 10179401 | 0.19516 | 33.9592 | 0.0852 | 24993 | 0.099 | 4917759 | 0.095667 | 13563.71 | 4.97 | 730.33 | 21194 | 534.5 | 4351.68 | 1.96
10 | 16983.25 | 3.97 | 10179792.9 | 0.0003919 | 33.9592 | 0 | 24993 | 0 | 5000823 | 0.083064 | 13567.89 | 4.18 | 730.34 | 21209 | 534.5 | 4354.65 | 2.97
11 | 16987.82 | 4.57 | 10279458 | 0.099665 | 34.024 | 0.0648 | 25149 | 0.156 | 5085009 | 0.084186 | 13572.59 | 4.7 | 730.91 | 22054 | 534.66 | 4354.65 | 0
12 | 16993 | 5.18 | 10582784 | 0.30333 | 34.0564 | 0.0324 | 25249 | 0.1 | 5184220 | 0.099211 | 13577.85 | 5.26 | 730.92 | 22069 | 534.65 | 4354.65 | 0
13 | 16998.33 | 5.33 | 10828823 | 0.24604 | 34.0564 | 0 | 25496 | 0.247 | 5283645 | 0.099425 | 13583.14 | 5.29 | 730.93 | 22084 | 584.66 | 4356.61 | 1.96
14 | 17003.45 | 5.12 | 10995334.2 | 0.16651 | 34.0863 | 0.0299 | 25496 | 0 | 5381888 | 0.098243 | 13588.48 | 5.34 | 730.94 | 22099 | 534.66 | 4360.17 | 3.56
15 | 17008.55 | 5.1 | 10995334.2 | 0 | 34.1494 | 0.0631 | 25496 | 0 | 5484006 | 0.10212 | 13593.51 | 5.03 | 730.95 | 22114 | 534.66 | 4363.74 | 3.57
16 | 17013.66 | 5.11 | 11192039 | 0.1967 | 34.1509 | 0.0015 | 25600 | 0.104 | 5583227 | 0.099221 | 13598.47 | 4.96 | 730.97 | 22143 | 534.67 | 4367.33 | 3.59
17 | 17018.63 | 4.97 | 11347944 | 0.1559 | 34.2188 | 0.0679 | 25756 | 0.156 | 5684395 | 0.10117 | 13603.84 | 5.37 | 730.99 | 22173 | 534.68 | 4370.95 | 3.62
18 | 17023.61 | 4.98 | 11623924 | 0.27598 | 34.2615 | 0.0427 | 25897 | 0.141 | 5779567 | 0.095172 | 13608.8 | 4.96 | 731 | 22188 | 534.69 | 4374.44 | 3.49
19 | 17027.71 | 4.1 | 11623924 | 0 | 34.2616 | 0.0001 | 25897 | 0 | 5864802 | 0.085235 | 13612.97 | 4.17 | 731.01 | 22203 | 534.68 | 4378.05 | 3.61
20 | 17032.83 | 5.12 | 11623924 | 0 | 34.2617 | 0.0001 | 25897 | 0 | 5963256 | 0.098454 | 13618.66 | 5.69 | 731 | 22188 | 534.66 | 4381.65 | 3.6
21 | 17037.79 | 4.96 | 11769559 | 0.14563 | 34.2772 | 0.0155 | 26032 | 0.135 | 6057993 | 0.094737 | 13623.53 | 4.87 | 731 | 22188 | 534.65 | 4385.13 | 3.48
22 | 17043 | 5.21 | 11924511 | 0.15495 | 34.2772 | 0 | 26143 | 0.111 | 6158659 | 0.10067 | 13628.64 | 5.11 | 731.01 | 22203 | 534.64 | 4388.79 | 3.66
23 | 17048.15 | 5.15 | 11924511 | 0 | 34.3111 | 0.0339 | 26231 | 0.088 | 6257020 | 0.098361 | 13633.88 | 5.24 | 731.04 | 22248 | 534.68 | 4392.38 | 3.59
24 | 17053.13 | 4.98 | 12151721 | 0.22721 | 34.3716 | 0.0605 | 26231 | 0 | 6353588 | 0.096568 | 13639.08 | 5.2 | 731.05 | 22263 | 534.67 | 4395.89 | 3.51
25 | 17058.22 | 5.09 | 12330976 | 0.17925 | 34.4263 | 0.0547 | 26337 | 0.106 | 6450628 | 0.09704 | 13644.49 | 5.41 | 731.05 | 22263 | 534.65 | 4399.47 | 3.58
26 | 17063.33 | 5.11 | 12405747 | 0.074771 | 34.4666 | 0.0403 | 26470 | 0.133 | 6546820 | 0.096192 | 13649.74 | 5.25 | 731.05 | 22263 | 534.66 | 4403.05 | 3.58
27 | 17068.3 | 4.97 | 12575845 | 0.1701 | 34.4667 | 0.0001 | 26594 | 0.124 | 6642501 | 0.095681 | 13654.64 | 4.9 | 731.05 | 22263 | 534.65 | 4404.63 | 1.58
28 | 17073.99 | 5.69 | 12665148 | 0.089303 | 34.4668 | 0.0001 | 26731 | 0.137 | 6740430 | 0.097929 | 13660.14 | 5.5 | 731.1 | 22337 | 534.67 | 4404.63 | 0
29 | 17077.97 | 3.98 | 12754493 | 0.089345 | 34.4669 | 0.0001 | 26731 | 0 | 6823808 | 0.083378 | 13664.42 | 4.28 | 731.08 | 22308 | 534.74 | 4404.63 | 0
30 | 17083.52 | 5.55 | 12845702 | 0.091209 | 34.5525 | 0.0856 | 26731 | 0 | 6929439 | 0.10563 | 13669.86 | 5.44 | 731.14 | 22397 | 534.73 | 4404.63 | 0
31 | 17088.99 | 5.47 | 12868037 | 0.022335 | 34.5528 | 0.0003 | 26731 | 0 | 7033443 | 0.104 | 13675.22 | 5.36 | 731.14 | 22397 | 534.73 | 4404.63 | 0
Totals | 527424.67 | 153.36 |  | 3.9418 |  | 0.8394 |  | 2.494 |  | 2.9554 |  | 155.47 |  |  |  |  | 71.61
Average | 17013.699 | 4.9471 |  | 0.12715 |  | 0.027077 |  | 0.080452 |  | 0.095335 |  | 5.0152 | 730.811 |  | 536.2429 |  | 2.31
Min |  | 3.24 |  | 0 |  | 0 |  | 0 |  | 0.072377 |  | 3.98 | 730.33 |  | 534.5 |  | 0
Max |  | 6.11 |  | 0.35351 |  | 0.0856 |  | 0.247 |  | 0.10563 |  | 5.73 | 731.14 |  | 584.66 |  | 5.05
Calculated Values
| Raw Water Added To System (MG) |  |  | 149.4182 |  |  | Raw to Potable Differential |  |  | -0.60237
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 150.0206 |  |  | Average Raw for Month |  |  | 4.9471
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.60837 |  |  | Peak Raw Flow for Month |  |  | 6.11
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | January/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 53 | 0 | 13.3333 | 7.91 | 2.305 | 0.0905 | 8.17 | 8.875 | 3.9792 | 135 | 90.0303 | 89 | 68.6667 | 8
2 | 47 | 0 | 14.1667 | 11.4 | 2.275 | 0.089 | 8.17 | 8.875 | 3.9567 | 127 | 136.3333 | 84 | 73.3333 | 9.6667
3 | 36 | 0 | 16.1667 | 9.51 | 2.355 | 0.0955 | 8.12 | 8.815 | 3.7358 | 125 | 137 | 85 | 71.3333 | 6
4 | 43 | 0 | 12.4384 | 12.1 | 2.3183 | 0.08 | 8.17 | 8.8467 | 3.6933 | 131 | 147 | 87 | 75 | 6.6667
5 | 43 | 0 | 14.1667 | 15 | 2.41 | 0.077167 | 8.24 | 8.8017 | 3.7933 | 130 | 143.6667 | 86 | 75.6667 | 4.6667
6 | 37 | 0 | 13.8333 | 14.6 | 2.2117 | 0.092333 | 8.18 | 8.765 | 3.8242 | 126 | 139 | 86 | 76 | 6.3333
7 | 43 | 0 | 14 | 10.6 | 1.985 | 0.092333 | 8.22 | 8.795 | 3.8433 | 140 | 139.3333 | 86 | 78.6667 | 5.3333
8 | 59 | 0 | 16.1667 | 12.9 | 1.8475 | 0.085333 | 8.16 | 8.7733 | 3.665 | 140 | 139 | 82 | 73.6667 | 5.6667
9 | 67 | 0 | 15.3333 | 12.7 | 1.944 | 0.097429 | 8.2 | 8.705 | 3.6758 | 128 | 142.6667 | 88 | 83 | 4.6667
10 | 44 | 1.6 | 15 | 15.7 | 1.795 | 0.10017 | 8.27 | 8.7883 | 3.6417 | 131 | 141.6667 | 84 | 80 | 5
11 | 35 | 0 | 14.5 | 22.4 | 1.83 | 0.074125 | 8.42 | 8.8267 | 3.5317 | 120 | 136 | 87 | 75.3333 | 2.6667
12 | 58 | 0 | 14.3333 | 14 | 2.185 | 0.11357 | 8.36 | 8.8517 | 3.8092 | 115 | 137.3333 | 87 | 74.3333 | 6.3333
13 | 59 | 0.1 | 14.5 | 11.8 | 1.7717 | 0.099333 | 8.55 | 8.838 | 3.7458 | 121 | 137.6667 | 88 | 74 | 3
14 | 64 | 0 | 14.8333 | 11.6 | 1.5583 | 0.096167 | 8.29 | 8.8567 | 3.725 | 123 | 144.6667 | 86 | 81 | 8
15 | 64 | 0 | 16.1667 | 11.1 | 1.53 | 0.10717 | 8.32 | 8.7967 | 3.6258 | 122 | 144.3333 | 84 | 81.3333 | 6.6667
16 | 81 | 0.7 | 15.6667 | 10.6 | 1.4183 | 0.075167 | 8.41 | 8.8717 | 3.5992 | 120 | 138 | 90 | 75.3333 | 7
17 | 59 | 0.25 | 16.3333 | 9.49 | 1.6483 | 0.090667 | 8.37 | 8.8083 | 3.7 | 132 | 140.3333 | 85 | 74.3333 | 5
18 | 36 | 0 | 15.1667 | 12 | 1.5933 | 0.10783 | 8.39 | 8.7833 | 3.7525 | 126 | 137 | 83 | 72.3333 | 4.6667
19 | 39 | 0 | 15 | 12.4 | 1.51 | 0.0905 | 8.34 | 8.755 | 3.635 | 121 | 136 | 86 | 75.3333 | 5.6667
20 | 37 | 0 | 15 | 10.5 | 1.4567 | 0.078 | 8.4 | 8.7267 | 3.6042 | 126 | 134.6667 | 88 | 75.6667 | 7.3333
21 | 43 | 0 | 14.8333 | 10.5 | 1.89 | 0.077 | 8.35 | 8.755 | 3.7625 | 132 | 137.3333 | 78 | 75.6667 | 7
22 | 48 | 0.45 | 14.8333 | 6.61 | 1.875 | 0.090667 | 8.34 | 8.8117 | 3.835 | 138 | 134 | 76 | 78.6667 | 6
23 | 41 | 0 | 14.3333 | 7.08 | 1.7942 | 0.086667 | 8.45 | 8.8067 | 3.7817 | 136 | 137.3333 | 80 | 77 | 8.6667
24 | 45 | 0 | 14.6667 | 6 | 1.5967 | 0.062833 | 8.55 | 8.7867 | 3.685 | 136 | 148.6667 | 86 | 77.6667 | 7
25 | 53 | 0 | 14.6667 | 6.22 | 1.7667 | 0.10362 | 8.47 | 8.815 | 3.7475 | 130 | 136.3333 | 87 | 74.3333 | 5.3333
26 | 46 | 0 | 14.6667 | 6.78 | 1.2008 | 0.085333 | 8.43 | 8.7867 | 3.73 | 118 | 136.6667 | 86 | 74 | 6.6667
27 | 55 | 0 | 16.1667 | 7.91 | 1.291 | 0.075667 | 8.53 | 8.83 | 3.6067 | 140 | 134 | 90 | 75 | 7.3333
28 | 41 | 0.65 | 14.6667 | 7.53 | 1.5533 | 0.084167 | 8.51 | 8.7967 | 3.745 | 144 | 142.3333 | 84 | 77.6667 | 6.3333
29 | 41 | 0 | 16.3333 | 8.6 | 1.364 | 0.059833 | 8.54 | 8.7867 | 3.3467 | 146 | 146 | 85 | 79.3333 | 5
30 | 41 | 0 | 14.3333 | 10 | 1.235 | 0.051167 | 8.55 | 8.765 | 3.4883 | 132 | 146.6667 | 85 | 79.6667 | 7
31 | 43 | 0 | 14.5 | 8.21 | 1.695 | 0.043 | 8.48 | 8.8233 | 3.6725 | 135 | 152.3333 | 88 | 85.3333 | 5.3333
TOTAL |  | 3.75
AVG. | 48.4194 | 0.12097 | 14.8421 | 10.7661 | 1.781 | 0.085556 | 8.3532 | 8.8038 | 3.7077 | 129.871 | 138.4956 | 85.3548 | 76.4086 | 6.129
MAX. | 81 | 1.6 | 16.3333 | 22.4 | 2.41 | 0.11357 | 8.55 | 8.875 | 3.9792 | 146 | 152.3333 | 90 | 85.3333 | 9.6667
MIN. | 35 | 0 | 12.4384 | 6 | 1.2008 | 0.043 | 8.12 | 8.705 | 3.3467 | 115 | 90.0303 | 76 | 68.6667 | 2.6667

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: January 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 3 | 24 | 100 | 0.51 | 108 | 1 | 32 | 1543.94 | 200 | 342 | 43 | 37.4746 | 8.3011 | 0.77671 | 4.8544 | 1.0437
2 | 3 | 24 | 100 | 0.05 | 92 | 1 | 34 | 1576.24 | 170 | 342 | 84 | 36.9136 | 8.0092 | 0.79624 | 3.9812 | 1.9672
3 | 3 | 15 | 0 | 0 | 0 | 0 | 22 | 981.92 | 150 | 213.75 | 60 | 36.3383 | 7.9103 | 0.81416 | 5.5511 | 2.2204
4 | 4 | 24 | 0 | 0 | 0 | 0 | 35 | 1918.62 | 280 | 555.75 | 30 | 37.8372 | 10.96 | 0.69024 | 5.5219 | 0.59163
5 | 3 | 19 | 101 | 0.96 | 122 | 1 | 22 | 1382.44 | 200 | 299.25 | 55 | 37.4177 | 8.0996 | 0.59546 | 5.4133 | 1.4887
6 | 3 | 21 | 0 | 0 | 0 | 0 | 23 | 1421.2 | 240 | 342 | 29 | 37.2069 | 8.9535 | 0.60214 | 6.2832 | 0.75922
7 | 3 | 24 | 110 | 0.51 | 133 | 1 | 30 | 1944.46 | 410 | 427.5 | 81 | 38.1585 | 8.3894 | 0.58873 | 8.0459 | 1.5896
8 | 4 | 17 | 100 | 0.53 | 112 | 1 | 20 | 1246.78 | 150 | 299.25 | 24 | 35.258 | 8.4626 | 0.56559 | 4.2419 | 0.6787
9 | 4 | 20 | 129 | 0.48 | 99 | 1 | 25 | 1569.78 | 220 | 342 | 31 | 38.3346 | 8.3518 | 0.61051 | 5.3725 | 0.75703
10 | 4 | 16 | 0 | 0 | 0 | 0 | 20 | 1279.08 | 200 | 256.5 | 55 | 38.6315 | 7.747 | 0.60405 | 6.0405 | 1.6611
11 | 4 | 17.5 | 97 | 0.72 | 156 | 1 | 22 | 1434.12 | 240 | 324.9 | 26 | 37.6273 | 8.5245 | 0.57722 | 6.2969 | 0.68217
12 | 3 | 24 | 107 | 0.51 | 100 | 1 | 27 | 1673.14 | 200 | 367.65 | 40 | 38.729 | 8.5102 | 0.62498 | 4.6295 | 0.9259
13 | 3 | 24 | 105 | 0.31 | 247 | 2 | 25 | 1582.7 | 220 | 367.65 | 56 | 35.6045 | 8.2707 | 0.5624 | 4.9491 | 1.2598
14 | 3 | 24 | 0 | 0 | 0 | 0 | 25 | 1563.32 | 220 | 410.4 | 43 | 36.611 | 9.6111 | 0.58547 | 5.1521 | 1.007
15 | 3 | 24 | 0 | 0 | 0 | 0 | 25 | 1582.7 | 230 | 342 | 47 | 37.2102 | 8.0406 | 0.58777 | 5.4074 | 1.105
16 | 3 | 24 | 101 | 0.23 | 104 | 1 | 25 | 1569.78 | 250 | 316.35 | 25 | 36.8343 | 7.423 | 0.58661 | 5.8661 | 0.58661
17 | 3 | 24 | 107 | 77.7 | 156 | 1 | 25 | 1582.7 | 220 | 470.25 | 20 | 38.1835 | 11.345 | 0.60314 | 5.3076 | 0.48251
18 | 3 | 24 | 0 | 0 | 0 | 0 | 25 | 1537.48 | 110 | 367.65 | 52 | 37.0181 | 8.852 | 0.60193 | 2.6485 | 1.252
19 | 3 | 19 | 0 | 0 | 0 | 0 | 22 | 1246.78 | 110 | 256.5 | 55 | 36.462 | 7.5013 | 0.64339 | 3.2169 | 1.6085
20 | 3 | 24 | 0 | 0 | 0 | 0 | 29 | 1576.24 | 260 | 333.45 | 23 | 36.9136 | 7.809 | 0.67914 | 6.0889 | 0.53863
21 | 3 | 24 | 118 | 0.48 | 135 | 1 | 29 | 1531.02 | 240 | 342 | 32 | 37.0112 | 8.2676 | 0.70105 | 5.8018 | 0.77357
22 | 3 | 24 | 105 | 0.59 | 111 | 1 | 29 | 1595.62 | 210 | 342 | 55 | 36.7219 | 7.8709 | 0.66741 | 4.833 | 1.2658
23 | 3 | 24 | 110 | 0.51 | 88 | 1 | 29 | 1582.7 | 270 | 342 | 55 | 36.849 | 7.9626 | 0.67519 | 6.2862 | 1.2805
24 | 3 | 24 | 0 | 0 | 0 | 0 | 29 | 1543.94 | 240 | 342 | 36 | 37.1736 | 8.2344 | 0.69824 | 5.7785 | 0.86678
25 | 3 | 24 | 96 | 0.01 | 106 | 1 | 29 | 1576.24 | 260 | 367.65 | 44 | 37.1312 | 8.6607 | 0.68315 | 6.1248 | 1.0365
26 | 3 | 24 | 114 | 0.48 | 133 | 1 | 29 | 1589.16 | 220 | 367.65 | 36 | 37.289 | 8.6268 | 0.68047 | 5.1622 | 0.84473
27 | 3 | 24 | 108 | 0.53 | 124 | 1 | 31 | 1524.56 | 440 | 324.9 | 49 | 36.7809 | 7.8384 | 0.74789 | 10.6153 | 1.1822
28 | 3 | 24 | 88 | 0.96 | 137 | 1 | 32 | 1782.96 | 320 | 367.65 | 55 | 37.5719 | 7.7474 | 0.67433 | 6.7433 | 1.159
29 | 3 | 24 | 0 | 0 | 0 | 0 | 31 | 1246.78 | 240 | 282.15 | 0 | 37.5613 | 8.5002 | 0.93393 | 7.2304 | 0
30 | 4 | 24 | 0 | 0 | 0 | 0 | 40 | 1750.66 | 340 | 384.75 | 55 | 37.8219 | 8.3123 | 0.86417 | 7.3455 | 1.1882
31 | 4 | 24 | 0 | 0 | 0 | 0 | 39 | 1744.2 | 300 | 384.75 | 21 | 38.2334 | 8.4338 | 0.85489 | 6.5761 | 0.46033
TOTAL |  | 696.5 |  |  | 2263 | 19 | 860 | 47681.26 | 7360 | 10824.3 | 1296
AVG | 3.2258 |  | 61.1613 | 2.7765 | 73 | 0.6129 | 27.7419 | 1481.6891 | 237.4194 | 340.4455 | 43.2 | 37.1553 | 8.4363 | 0.67344 | 5.7215 | 1.0407
MIN | 3 |  | 0 | 0 | 0 | 0 | 20 | 981.92 | 110 | 213.75 | 0 | 35.6045 | 7.423 | 0.5624 | 2.6485 | 0
MAX | 4 |  | 129 | 77.7 | 247 | 2 | 40 | 1944.46 | 440 | 555.75 | 84 | 38.729 | 11.345 | 0.93393 | 10.6153 | 2.2204

## Monthly Chemical Report
Month, Year: |  | January/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #REF!
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 4.94 | 327.36 | 7.0906 | 35.0275 | 3087.88 | 59.0698 | 291.8047 | 200 | 14.5547 | 71.9 | 342 | 50.5385 | 249.66 | [9 empty] | 43 | 16.2773 | 80.41 | 163.02 | 147.5308 | 891.8222
2 | 5.12 | 347.82 | 7.2689 | 37.2167 | 3152.48 | 58.1854 | 297.9094 | 170 | 11.9365 | 61.115 | 342 | 48.7617 | 249.66 | [9 empty] | 84 | 30.6797 | 157.08 | 168.96 | 156.8322 | 971.9411
3 | 3.24 | 225.06 | 7.4325 | 24.0814 | 1963.84 | 57.2787 | 185.5829 | 150 | 16.6435 | 53.925 | 213.75 | 48.1597 | 156.0375 | [9 empty] | 60 | 34.6296 | 112.2 | 106.92 | 164.1441 | 638.7468
4 | 6.08 | 358.05 | 6.3012 | 38.3113 | 3837.24 | 59.6413 | 362.6192 | 280 | 16.5559 | 100.66 | 555.75 | 66.7266 | 405.6975 | [9 empty] | 30 | 9.227 | 56.1 | 200.64 | 158.452 | 1164.028
5 | 4.43 | 225.06 | 5.436 | 24.0814 | 2764.88 | 58.9799 | 261.2812 | 200 | 16.2302 | 71.9 | 299.25 | 49.3121 | 218.4525 | [9 empty] | 55 | 23.2167 | 102.85 | 146.19 | 153.175 | 824.7551
6 | 4.58 | 235.29 | 5.4969 | 25.176 | 2842.4 | 58.6478 | 268.6068 | 240 | 18.8384 | 86.28 | 342 | 54.5109 | 249.66 | [9 empty] | 29 | 11.8406 | 54.23 | 151.14 | 149.3347 | 835.0928
7 | 6.11 | 306.9 | 5.3745 | 32.8383 | 3888.92 | 60.1478 | 367.5029 | 410 | 24.1236 | 147.395 | 427.5 | 51.0761 | 312.075 | [9 empty] | 81 | 24.7905 | 151.47 | 201.63 | 165.5125 | 1212.9112
8 | 4.24 | 204.6 | 5.1633 | 21.8922 | 2493.56 | 55.5758 | 235.6414 | 150 | 12.7182 | 53.925 | 299.25 | 51.5218 | 218.4525 | [9 empty] | 24 | 10.5849 | 44.88 | 139.92 | 135.5639 | 714.7111
9 | 4.91 | 255.75 | 5.5734 | 27.3652 | 3139.56 | 60.4253 | 296.6884 | 220 | 16.1079 | 79.09 | 342 | 50.8473 | 249.66 | [9 empty] | 31 | 11.8065 | 57.97 | 162.03 | 144.7604 | 872.8037
10 | 3.97 | 204.6 | 5.5144 | 21.8922 | 2558.16 | 60.8932 | 241.7461 | 200 | 18.1108 | 71.9 | 256.5 | 47.165 | 187.245 | [9 empty] | 55 | 25.9068 | 102.85 | 131.01 | 157.5903 | 756.6433
11 | 4.57 | 225.06 | 5.2695 | 24.0814 | 2868.24 | 59.3104 | 271.0487 | 240 | 18.8796 | 86.28 | 324.9 | 51.8987 | 237.177 | [9 empty] | 26 | 10.6389 | 48.62 | 150.81 | 145.9972 | 818.0171
12 | 5.18 | 276.21 | 5.7055 | 29.5545 | 3346.28 | 61.047 | 316.2235 | 200 | 13.8803 | 71.9 | 367.65 | 51.8117 | 268.3845 | [9 empty] | 40 | 14.4402 | 74.8 | 170.94 | 146.8846 | 931.8024
13 | 5.33 | 255.75 | 5.1342 | 27.3652 | 3165.4 | 56.122 | 299.1303 | 220 | 14.8386 | 79.09 | 367.65 | 50.3536 | 268.3845 | [9 empty] | 56 | 19.6473 | 104.72 | 175.89 | 146.0957 | 954.5801
14 | 5.12 | 255.75 | 5.3448 | 27.3652 | 3126.64 | 57.7085 | 295.4675 | 220 | 15.4473 | 79.09 | 410.4 | 58.5141 | 299.592 | [9 empty] | 43 | 15.7051 | 80.41 | 168.96 | 152.7197 | 950.8847
15 | 5.1 | 255.75 | 5.3657 | 27.3652 | 3165.4 | 58.653 | 299.1303 | 230 | 16.2127 | 82.685 | 342 | 48.9529 | 249.66 | [9 empty] | 47 | 17.2333 | 87.89 | 168.3 | 146.4178 | 915.0305
16 | 5.11 | 255.75 | 5.3552 | 27.3652 | 3139.56 | 58.0604 | 296.6884 | 250 | 17.5881 | 89.875 | 316.35 | 45.1929 | 230.9355 | [9 empty] | 25 | 9.1487 | 46.75 | 168.63 | 135.3452 | 860.2442
17 | 4.97 | 255.75 | 5.5061 | 27.3652 | 3165.4 | 60.1872 | 299.1303 | 220 | 15.9135 | 79.09 | 470.25 | 69.0709 | 343.2825 | [9 empty] | 20 | 7.5252 | 37.4 | 164.01 | 158.2028 | 950.2781
18 | 4.98 | 255.75 | 5.495 | 27.3652 | 3074.96 | 58.3501 | 290.5837 | 110 | 7.9408 | 39.545 | 367.65 | 53.8925 | 268.3845 | [9 empty] | 52 | 19.5261 | 97.24 | 164.34 | 145.2045 | 887.4585
19 | 4.1 | 225.06 | 5.8735 | 24.0814 | 2493.56 | 57.4735 | 235.6414 | 110 | 9.6451 | 39.545 | 256.5 | 45.6695 | 187.245 | [9 empty] | 55 | 25.0854 | 102.85 | 135.3 | 143.747 | 724.6628
20 | 5.12 | 296.67 | 6.1999 | 31.7437 | 3152.48 | 58.1854 | 297.9094 | 260 | 18.2559 | 93.47 | 333.45 | 47.5427 | 243.4185 | [9 empty] | 23 | 8.4004 | 43.01 | 168.96 | 138.5843 | 878.5116
21 | 4.96 | 296.67 | 6.3999 | 31.7437 | 3062.04 | 58.3393 | 289.3628 | 240 | 17.3952 | 86.28 | 342 | 50.3347 | 249.66 | [9 empty] | 32 | 12.0645 | 59.84 | 163.68 | 144.5336 | 880.5665
22 | 5.21 | 296.67 | 6.0928 | 31.7437 | 3191.24 | 57.8833 | 301.5722 | 210 | 14.4904 | 75.495 | 342 | 47.9194 | 249.66 | [9 empty] | 55 | 19.7409 | 102.85 | 171.93 | 146.1268 | 933.2509
23 | 5.15 | 296.67 | 6.1638 | 31.7437 | 3165.4 | 58.0836 | 299.1303 | 270 | 18.8476 | 97.065 | 342 | 48.4777 | 249.66 | [9 empty] | 55 | 19.9709 | 102.85 | 169.95 | 151.5435 | 950.399
24 | 4.98 | 296.67 | 6.3742 | 31.7437 | 3087.88 | 58.5953 | 291.8047 | 240 | 17.3253 | 86.28 | 342 | 50.1325 | 249.66 | [9 empty] | 36 | 13.5181 | 67.32 | 164.34 | 145.9455 | 891.1483
25 | 5.09 | 296.67 | 6.2365 | 31.7437 | 3152.48 | 58.5284 | 297.9094 | 260 | 18.3635 | 93.47 | 367.65 | 52.7278 | 268.3845 | [9 empty] | 44 | 16.165 | 82.28 | 167.97 | 152.0211 | 941.7576
26 | 5.11 | 296.67 | 6.2121 | 31.7437 | 3178.32 | 58.7772 | 300.3512 | 220 | 15.4775 | 79.09 | 367.65 | 52.5214 | 268.3845 | [9 empty] | 36 | 13.1742 | 67.32 | 168.63 | 146.1623 | 915.5194
27 | 4.97 | 317.13 | 6.8275 | 33.9329 | 3049.12 | 57.9762 | 288.1418 | 440 | 31.827 | 158.18 | 324.9 | 47.7217 | 237.177 | [9 empty] | 49 | 18.4366 | 91.63 | 164.01 | 162.7891 | 973.0717
28 | 5.69 | 327.36 | 6.156 | 35.0275 | 3565.92 | 59.2231 | 336.9794 | 320 | 20.2179 | 115.04 | 367.65 | 47.1678 | 268.3845 | [9 empty] | 55 | 18.0756 | 102.85 | 187.77 | 150.8403 | 1046.0515
29 | 3.98 | 317.13 | 8.5259 | 33.9329 | 2493.56 | 59.2064 | 235.6414 | 240 | 21.6784 | 86.28 | 282.15 | 51.7511 | 205.9695 | [9 empty] | 0 | 0 | 0 | 131.34 | 141.1618 | 693.1638
30 | 5.55 | 409.2 | 7.8891 | 43.7844 | 3501.32 | 59.6171 | 330.8747 | 340 | 22.0234 | 122.23 | 384.75 | 50.6068 | 280.8675 | [9 empty] | 55 | 18.5315 | 102.85 | 183.15 | 158.6679 | 1063.7566
31 | 5.47 | 398.97 | 7.8043 | 42.6898 | 3488.4 | 60.2658 | 329.6538 | 300 | 19.7166 | 107.85 | 384.75 | 51.3469 | 280.8675 | [9 empty] | 21 | 7.1792 | 39.27 | 180.51 | 146.3128 | 980.8411
Total | 153.36 |  |  | 941.3646 |  |  | 9011.7581 |  |  | 2645.92 |  |  | 7901.739 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 2462.79 | 5060.88 | 4638.1993 | 28024.4517
Avg. | 4.9471 | 283.8 | 6.1479 | 30.3666 | 3076.2103 | 58.7238 | 290.7019 | 237.4194 | 17.1543 | 85.3523 | 349.171 | 51.3622 | 254.8948 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 42.4839 | 16.2312 | 79.4448 | 163.2542 | 182.7364 | 904.0146
Max | 6.11 | 409.2 | 8.5259 | 43.7844 | 3888.92 | 61.047 | 367.5029 | 440 | 31.827 | 158.18 | 555.75 | 69.0709 | 405.6975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 34.6296 | 157.08 | 201.63 | 165.5125 | 1212.9112
Min. | 3.24 | 204.6 | 5.1342 | 21.8922 | 1963.84 | 55.5758 | 185.5829 | 110 | 7.9408 | 39.545 | 213.75 | 45.1929 | 156.0375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.92 | 135.3452 | 638.7468
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 1.87 | Lime | 33 | Per MGD
|  | Contract through |  | Brenntag | Contract through |  | Pencco | Contract through |  | DPC | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  | Brenntag | Contract | Texas Lime | 0.18274 | PerKG

## LAS Meter
LAS carrier water meter
0 | 6020810
1 | 6060460 | 39650
2 | 6100730 | 40270
3 | 6125380 | 24650
4 | 6165990 | 40610
5 | 6199100 | 33110
6 | 6235240 | 36140
7 | 6276440 | 41200
8 | 6305740 | 29300
9 | 6339150 | 33410
10 | 6366190 | 27040
11 | 6396620 | 30430
12 | 6437190 | 40570
13 | 6477570 | 40380
14 | 6517560 | 39990
15 | 6557680 | 40120
16 | 6598230 | 40550
17 | 6639230 | 41000
18 | 6678650 | 39420
19 | 6711120 | 32470
20 | 6751740 | 40620
21 | 6790870 | 39130
22 | 6831990 | 41120
23 | 6872630 | 40640
24 | 6911980 | 39350
25 | 6952270 | 40290
26 | 6992599 | 40329
27 | 7031440 | 38841
28 | 7072750 | 41310
29 | 7103270 | 30520
30 | 7143560 | 40290
31 | 7183970 | 40410
Total |  | 1163160

## Graphs
Chemicals | Amount
LAS | 1737.1256
Fe | 9011.7581
CL2 | 2645.92
Poly | 7901.739
Potassium | 2462.79
Lime | 0
Chemfloc 3315 | 28024.4517