## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: July 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 17926.98 |  | 4063086 |  | 38.2768 |  | 40880 |  | 1337967 |  | 406.5215 |  |  |  |  | 4712.88
1 | 17935.48 | 8.5 | 4063086 | 0 | 38.3192 | 0.0424 | 40880 | 0 | 1483897 | 0.14593 | 414.5161 | 7.9946 | 733.69 | 26306 | 537.46 | 4716.34 | 3.46
2 | 17942.09 | 6.61 | 4107670 | 0.044584 | 38.3193 | 0.0001 | 40880 | 0 | 1625244 | 0.14135 | 421.4831 | 6.967 | 733.67 | 26275 | 537.45 | 4719.86 | 3.52
3 | 17949.48 | 7.39 | 4574300 | 0.46663 | 38.3837 | 0.0644 | 41270 | 0.39 | 1770018 | 0.14477 | 428.8914 | 7.4083 | 733.66 | 26259 | 537.44 | 4723.31 | 3.45
4 | 17955.91 | 6.43 | 4639870 | 0.06557 | 38.4253 | 0.0416 | 41270 | 0 | 1913130 | 0.14311 | 435.8159 | 6.9245 | 733.64 | 26228 | 537.41 | 4726.76 | 3.45
5 | 17963.13 | 7.22 | 4945164 | 0.30529 | 38.4255 | 0.0002 | 41530 | 0.26 | 2057890 | 0.14476 | 443.3084 | 7.4925 | 733.62 | 26196 | 537.39 | 4730.23 | 3.47
6 | 17970.6 | 7.47 | 5014407 | 0.069243 | 38.4255 | 0 | 41644 | 0.114 | 2207759 | 0.14987 | 450.3108 | 7.0024 | 733.61 | 26181 | 537.37 | 4733.71 | 3.48
7 | 17976.15 | 5.55 | 5185931 | 0.17152 | 38.4867 | 0.0612 | 41644 | 0 | 2355070 | 0.14731 | 456.5793 | 6.2685 | 733.61 | 26181 | 537.69 | 4737.24 | 3.53
8 | 17982.59 | 6.44 | 5349513 | 0.16358 | 38.4867 | 0 | 41751 | 0.107 | 2499580 | 0.14451 | 463.0968 | 6.5175 | 733.61 | 26181 | 537.28 | 4740.7 | 3.46
9 | 17990.07 | 7.48 | 5413428 | 0.063915 | 38.5161 | 0.0294 | 41826 | 0.075 | 2645380 | 0.1458 | 470.1929 | 7.0961 | 733.57 | 26118 | 538.27 | 4744.15 | 3.45
10 | 17996.73 | 6.66 | 5657609 | 0.24418 | 38.5883 | 0.0722 | 41908 | 0.082 | 2795248 | 0.14987 | 477.2008 | 7.0079 | 733.56 | 26102 | 538.25 | 4747.68 | 3.53
11 | 18003.32 | 6.59 | 5733144 | 0.075535 | 38.5984 | 0.0101 | 41986 | 0.078 | 2939062 | 0.14381 | 484.2804 | 7.0796 | 733.55 | 26087 | 538.22 | 4751.1 | 3.42
12 | 18010.4 | 7.08 | 5804891 | 0.071747 | 38.5984 | 0 | 42120 | 0.134 | 3086100 | 0.14704 | 491.464 | 7.1836 | 733.55 | 26087 | 538.22 | 4754.59 | 3.49
13 | 18017.97 | 7.57 | 6075200 | 0.27031 | 38.6459 | 0.0475 | 42312 | 0.192 | 3231770 | 0.14567 | 499.158 | 7.694 | 733.48 | 25977 | 538.04 | 4758.06 | 3.47
14 | 18025.9 | 7.93 | 6279431 | 0.20423 | 38.6459 | 0 | 42470 | 0.158 | 3380950 | 0.14918 | 507.0528 | 7.8948 | 733.44 | 25915 | 537.93 | 4761.57 | 3.51
15 | 18033.38 | 7.48 | 6421239 | 0.14181 | 38.7073 | 0.0614 | 42470 | 0 | 3528224 | 0.14727 | 514.5647 | 7.5119 | 733.4 | 25852 | 537.86 | 4765.04 | 3.47
16 | 18041.86 | 8.48 | 6536618 | 0.11538 | 38.7818 | 0.0745 | 42548 | 0.078 | 3677550 | 0.14933 | 522.6417 | 8.077 | 733.36 | 25790 | 537.83 | 4768.46 | 3.42
17 | 18048.89 | 7.03 | 6761815 | 0.2252 | 38.7818 | 0 | 42703 | 0.155 | 3827370 | 0.14982 | 530.3698 | 7.7281 | 733.33 | 25743 | 537.8 | 4771.99 | 3.53
18 | 18057.19 | 8.3 | 7002818 | 0.241 | 38.7818 | 0 | 42903 | 0.2 | 3975290 | 0.14792 | 538.2115 | 7.8417 | 733.29 | 25680 | 537.76 | 4775.37 | 3.38
19 | 18064.77 | 7.58 | 7243823 | 0.241 | 38.7819 | 0.0001 | 43069 | 0.166 | 4125746 | 0.15046 | 546.0874 | 7.8759 | 733.27 | 25649 | 537.73 | 4778.83 | 3.46
20 | 18071.81 | 7.04 | 7325539 | 0.081716 | 38.8234 | 0.0415 | 43069 | 0 | 4278670 | 0.15292 | 553.498 | 7.4106 | 733.23 | 25587 | 537.7 | 4782.3 | 3.47
21 | 18079.83 | 8.02 | 7678507 | 0.35297 | 38.8619 | 0.0385 | 43257 | 0.188 | 4435920 | 0.15725 | 561.5754 | 8.0774 | 733.19 | 25525 | 537.66 | 4785.78 | 3.48
22 | 18087.83 | 8 | 7864112 | 0.1856 | 38.8649 | 0.003 | 43501 | 0.244 | 4594562 | 0.15864 | 569.4669 | 7.8915 | 733.17 | 25493 | 537.64 | 4789.24 | 3.46
23 | 18095.89 | 8.06 | 7939139 | 0.075027 | 38.9381 | 0.0732 | 43501 | 0 | 4746691 | 0.15213 | 577.7225 | 8.2556 | 733.14 | 25447 | 537.61 | 4792.71 | 3.47
24 | 18103.85 | 7.96 | 8045902 | 0.10676 | 39.0138 | 0.0757 | 43501 | 0 | 4896262 | 0.14957 | 585.922 | 8.1995 | 733.1 | 25385 | 537.59 | 4796.18 | 3.47
25 | 18111.93 | 8.08 | 8281084 | 0.23518 | 39.0805 | 0.0667 | 43665 | 0.164 | 5044530 | 0.14827 | 594.2063 | 8.2843 | 733.07 | 25338 | 537.54 | 4799.65 | 3.47
26 | 18120.67 | 8.74 | 8355529 | 0.074445 | 39.0805 | 0 | 43665 | 0 | 5199155 | 0.15463 | 603.2491 | 9.0428 | 733.09 | 25342 | 537.51 | 4803.08 | 3.43
27 | 18129.56 | 8.89 | 8517292 | 0.16176 | 39.1113 | 0.0308 | 43665 | 0 | 5350515 | 0.15136 | 611.972 | 8.7229 | 733.07 | 25358 | 537.59 | 4806.53 | 3.45
28 | 18136.33 | 6.77 | 8674666 | 0.15737 | 39.1621 | 0.0508 | 43899 | 0.234 | 5501630 | 0.15111 | 619.3037 | 7.3317 | 733.05 | 25307 | 537.55 | 4810 | 3.47
29 | 18144.44 | 8.11 | 8829372 | 0.15471 | 39.2008 | 0.0387 | 44029 | 0.13 | 5654100 | 0.15247 | 627.2495 | 7.9458 | 733.04 | 25292 | 537.53 | 4813.49 | 3.49
30 | 18152.45 | 8.01 | 9231472 | 0.4021 | 39.2615 | 0.0607 | 44226 | 0.197 | 5799885 | 0.14578 | 635.4855 | 8.236 | 733 | 25229 | 537.48 | 4816.9 | 3.41
31 | 18161.04 | 8.59 | 9403462 | 0.17199 | 39.3015 | 0.04 | 44368 | 0.142 | 5945450 | 0.14556 | 644.1895 | 8.704 | 732.96 | 25168 | 537.46 | 4820.36 | 3.46
Totals | 559361.54 | 234.06 |  | 5.3404 |  | 1.0247 |  | 3.488 |  | 4.6075 |  | 237.668 |  |  |  |  | 107.48
Average | 18043.9206 | 7.5503 |  | 0.17227 |  | 0.033055 |  | 0.11252 |  | 0.14863 |  | 7.6667 | 733.3555 |  | 537.6858 |  | 3.4671
Min |  | 5.55 |  | 0 |  | 0 |  | 0 |  | 0.14135 |  | 6.2685 | 732.96 |  | 537.28 |  | 3.38
Max |  | 8.89 |  | 0.46663 |  | 0.0757 |  | 0.39 |  | 0.15864 |  | 9.0428 | 733.69 |  | 538.27 |  | 3.53
Calculated Values
| Raw Water Added To System (MG) |  |  | 228.7196 |  |  | Raw to Potable Differential |  |  | -0.85289
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 229.5725 |  |  | Average Raw for Month |  |  | 7.5503
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.82768 |  |  | Peak Raw Flow for Month |  |  | 8.89
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | July/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 82 | 0 | 25.3333 | 9.04 | 2.3133 | 0.085667 | 8.59 | 9.0183 | 3.7483 | 140 | 132.3333 | 105 | 74.6667 | 10
2 | 78 | 0 | 25.5 | 8.45 | 1.8725 | 0.079833 | 8.63 | 9.0467 | 3.6308 | 136 | 133.3333 | 98 | 73.3333 | 7
3 | 73 | 0 | 25.8333 | 7.08 | 1.9617 | 0.079 | 8.82 | 8.9667 | 3.5317 | 142 | 138 | 110 | 76.3333 | 6.3333
4 | 84 | 0 | 26.6667 | 6.57 | 1.5667 | 0.093333 | 8.92 | 8.9317 | 3.4742 | 122 | 130.3333 | 93 | 71.6667 | 10
5 | 87 | 0.1 | 26.8333 | 3.98 | 1.9917 | 0.0925 | 8.72 | 8.985 | 3.2833 | 130 | 124.6667 | 96 | 69.3333 | 8.6667
6 | 73 | 0.3 | 26 | 7.03 | 2.765 | 0.069333 | 8.52 | 8.9733 | 3.4783 | 128 | 137.6667 | 92 | 72.6667 | 10.3333
7 | 75 | 0.5 | 25.6667 | 4.81 | 1.9917 | 0.070571 | 8.22 | 9.0633 | 3.3375 | 134 | 125 | 96 | 61.3333 | 8.3333
8 | 84 | 0 | 26.6667 | 5.86 | 1.5333 | 0.097833 | 8.4 | 9.0267 | 3.5575 | 121 | 123.3333 | 92 | 60 | 8.6667
9 | 77 | 0 | 25.5 | 8.22 | 1.9867 | 0.095833 | 8.65 | 8.9333 | 3.4783 | 123 | 121.6667 | 114 | 66.3333 | 7.6667
10 | 81 | 0 | 27 | 6.54 | 1.9317 | 0.069167 | 8.65 | 8.9233 | 3.315 | 120 | 119.6667 | 92 | 68 | 11
11 | 79 | 0 | 26.6667 | 5.99 | 1.6367 | 0.0965 | 8.71 | 8.98 | 3.4717 | 116 | 118 | 90 | 61 | 7.3333
12 | 79 | 0 | 26 | 6.92 | 1.8583 | 0.072 | 8.66 | 9.01 | 3.5492 | 120 | 118.3333 | 86 | 67.6667 | 9
13 | 84 | 0 | 27.3333 | 6.06 | 1.8717 | 0.086 | 8.82 | 8.9883 | 3.3933 | 114 | 89.6667 | 93 | 70.3333 | 7.6667
14 | 84 | 0 | 27.8333 | 7.65 | 1.9583 | 0.12233 | 8.85 | 8.885 | 3.65 | 131 | 132 | 98 | 71 | 6.6667
15 | 84 | 0 | 25.5 | 7.76 | 1.6267 | 0.078 | 8.48 | 8.89 | 3.405 | 116 | 122.3333 | 94 | 67.3333 | 9.3333
16 | 81 | 0 | 27.5 | 7.25 | 1.9317 | 0.084167 | 8.24 | 8.8233 | 3.7933 | 115 | 121 | 93 | 61.6667 | 8.6667
17 | 84 | 0 | 26.5 | 8.66 | 2.0783 | 0.074167 | 8.38 | 8.99 | 3.5092 | 125 | 109.3333 | 92 | 63.6667 | 10
18 | 84 | 0 | 26 | 8.92 | 2.23 | 0.070667 | 8.51 | 8.9183 | 3.365 | 117 | 119.3333 | 93 | 69.6667 | 10
19 | 82 | 0 | 25.8333 | 5.56 | 2.2517 | 0.073833 | 8.46 | 8.8433 | 3.5992 | 115 | 124 | 94 | 70.3333 | 8.3333
20 | 77 | 0 | 26.8333 | 8.09 | 1.8017 | 0.095833 | 8.54 | 9.0567 | 3.6633 | 114 | 125 | 95 | 55.6667 | 8.3333
21 | 79 | 0 | 26.1667 | 8.09 | 2.16 | 0.11483 | 8.43 | 8.56 | 3.4575 | 130 | 131.6667 | 100 | 71 | 6
22 | 81 | 0 | 27.1667 | 6.74 | 1.9783 | 0.10567 | 8.62 | 8.74 | 3.545 | 132 | 131.3333 | 100 | 65 | 6
23 | 83 | 0 | 25.3333 | 8.44 | 2.2 | 0.094833 | 8.51 | 8.98 | 3.8125 | 120 | 118.6667 | 92 | 60.3333 | 7.3333
24 | 88 | 0 | 26.8333 | 7.15 | 2.285 | 0.10283 | 8.73 | 9.0633 | 3.7725 | 122 | 114.6667 | 91 | 60.3333 | 7
25 | 80 | 0.2 | 26.6667 | 5.15 | 2.0217 | 0.082 | 8.12 | 8.9467 | 3.6775 | 125 | 116.3333 | 105 | 64 | 8.3333
26 | 80 | 0 | 25.8333 | 7.23 | 2.3067 | 0.11033 | 8.37 | 8.6033 | 3.0783 | 110 | 127.3333 | 87 | 77.6667 | 6.3333
27 | 82 | 0 | 26.1667 | 6.17 | 2.3517 | 0.099167 | 8.45 | 8.9817 | 3.415 | 112 | 113.6667 | 89 | 62.3333 | 6.6667
28 | 79 | 0 | 27 | 6.51 | 2.604 | 0.094333 | 8.37 | 8.7667 | 3.8158 | 125 | 118.3333 | 88 | 66 | 7.6667
29 | 77 | 0 | 26.6667 | 5.65 | 2.0817 | 0.15717 | 8.23 | 8.645 | 3.7683 | 110 | 108.3333 | 85 | 62.6667 | 11.6667
30 | 88 | 0 | 27 | 6.27 | 1.9967 | 0.0925 | 8.28 | 8.99 | 3.8683 | 115 | 108.3333 | 87 | 53 | 6.6667
31 | 68 | 0 | 27.8333 | 6.54 | 1.88 | 0.085167 | 8.43 | 8.8733 | 3.15 | 115 | 119.3333 | 87 | 59 | 9
TOTAL |  | 1.1
AVG. | 80.5484 | 0.035484 | 26.4409 | 6.9155 | 2.0331 | 0.091142 | 8.5261 | 8.9162 | 3.5353 | 122.4194 | 121.7097 | 94.4194 | 66.2366 | 8.2581
MAX. | 88 | 0.5 | 27.8333 | 9.04 | 2.765 | 0.15717 | 8.92 | 9.0633 | 3.8683 | 142 | 138 | 114 | 77.6667 | 11.6667
MIN. | 68 | 0 | 25.3333 | 3.98 | 1.5333 | 0.069167 | 8.12 | 8.56 | 3.0783 | 110 | 89.6667 | 85 | 53 | 6

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: July 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 5 | 24 | 0 | 0 | 0 | 0 | 82 | 2810.1 | 500 | 666.9 | 95 | 39.6403 | 9.4075 | 1.1567 | 7.0532 | 1.3401
2 | 5 | 18 | 0 | 0 | 0 | 0 | 61 | 3998.74 | 520 | 581.4 | 93 | 72.5363 | 10.5465 | 1.1065 | 9.4327 | 1.687
3 | 4 | 24 | 118 | 2.25 | 390 | 3 | 72 | 2577.54 | 580 | 624.15 | 84 | 41.821 | 10.1269 | 1.1682 | 9.4106 | 1.3629
4 | 4 | 24 | 0 | 0 | 0 | 0 | 57 | 2189.94 | 480 | 538.65 | 64 | 40.8371 | 10.0445 | 1.0629 | 8.9508 | 1.1934
5 | 5 | 24 | 0 | 0 | 0 | 0 | 46 | 2454.8 | 520 | 555.75 | 81 | 40.7674 | 9.2295 | 0.76393 | 8.6358 | 1.3452
6 | 4 | 24 | 110 | 0.72 | 114 | 1 | 65 | 2622.76 | 540 | 624.15 | 63 | 42.099 | 10.0185 | 1.0433 | 8.6678 | 1.0112
7 | 4 | 24 | 0 | 0 | 0 | 0 | 48 | 1963.84 | 460 | 470.25 | 55 | 42.4275 | 10.1594 | 1.037 | 9.938 | 1.1882
8 | 4 | 24 | 111 | 0.75 | 107 | 1 | 57 | 2254.54 | 460 | 513 | 55 | 41.9765 | 9.5514 | 1.0613 | 8.5646 | 1.024
9 | 5 | 24 | 97 | 0.51 | 75 | 1 | 66 | 2577.54 | 140 | 581.4 | 67 | 41.3179 | 9.3198 | 1.058 | 2.2442 | 1.074
10 | 4 | 24 | 120 | 0.48 | 83 | 1 | 56 | 2312.68 | 260 | 555.75 | 78 | 41.6366 | 10.0055 | 1.0082 | 4.6809 | 1.4043
11 | 4 | 24 | 110 | 0.48 | 77 | 1 | 55 | 2261 | 320 | 581.4 | 106 | 41.1386 | 10.5785 | 1.0007 | 5.8224 | 1.9287
12 | 4 | 24 | 113 | 3.22 | 134 | 1 | 58 | 2422.5 | 640 | 555.75 | 106 | 41.0265 | 9.412 | 0.98227 | 10.8388 | 1.7952
13 | 5 | 24 | 102 | 0.81 | 192 | 2 | 63 | 2596.92 | 500 | 855 | 47 | 41.1336 | 13.5427 | 0.99788 | 7.9197 | 0.74445
14 | 5 | 24 | 97 | 0.8 | 158 | 1 | 65 | 2784.26 | 560 | 837.9 | 109 | 42.0989 | 12.6693 | 0.98282 | 8.4674 | 1.6481
15 | 5 | 24 | 0 | 0 | 0 | 0 | 63 | 2590.46 | 540 | 538.65 | 92 | 41.525 | 8.6345 | 1.0099 | 8.6562 | 1.4748
16 | 5 | 24 | 108 | 0.48 | 58 | 1 | 69 | 2919.92 | 640 | 709.65 | 130 | 41.2866 | 10.0342 | 0.97563 | 9.0494 | 1.8382
17 | 5 | 24 | 94 | 5.78 | 155 | 1 | 53 | 2454.8 | 400 | 538.65 | 145 | 41.8692 | 9.1872 | 0.90397 | 6.8224 | 2.4731
18 | 5 | 24 | 115 | 0.45 | 200 | 2 | 68 | 2861.78 | 560 | 812.25 | 110 | 41.3421 | 11.734 | 0.98235 | 8.0899 | 1.5891
19 | 5 | 24 | 112 | 0.96 | 166 | 1 | 61 | 2667.98 | 440 | 555.75 | 74 | 42.2034 | 8.7911 | 0.96493 | 6.9601 | 1.1706
20 | 5 | 24 | 0 | 0 | 0 | 0 | 55 | 2403.12 | 380 | 513 | 91 | 40.9295 | 8.7373 | 0.93675 | 6.4721 | 1.5499
21 | 5 | 24 | 113 | 1.01 | 188 | 2 | 60 | 2777.8 | 620 | 624.15 | 85 | 41.5299 | 9.3314 | 0.89704 | 9.2694 | 1.2708
22 | 5 | 24 | 100 | 0.06 | 244 | 2 | 60 | 2777.8 | 510 | 598.5 | 103 | 41.6337 | 8.9703 | 0.89928 | 7.6439 | 1.5438
23 | 5 | 24 | 0 | 0 | 0 | 0 | 60 | 2764.88 | 730 | 555.75 | 87 | 41.1316 | 8.2676 | 0.89259 | 10.8598 | 1.2942
24 | 5 | 24 | 0 | 0 | 0 | 0 | 58 | 2777.8 | 300 | 641.25 | 110 | 41.8429 | 9.6594 | 0.87367 | 4.519 | 1.657
25 | 5 | 24 | 133 | 3.77 | 164000 | 2 | 56 | 2803.64 | 470 | 624.15 | 137 | 41.6049 | 9.2621 | 0.83102 | 6.9746 | 2.033
26 | 5 | 24 | 0 | 0 | 0 | 0 | 63 | 2965.14 | 370 | 709.65 | 138 | 40.6788 | 9.7357 | 0.8643 | 5.076 | 1.8932
27 | 5 | 24 | 0 | 0 | 0 | 0 | 64 | 3630.52 | 960 | 684 | 150 | 48.9667 | 9.2255 | 0.8632 | 12.948 | 2.0231
28 | 5 | 20.5 | 136 | 0.55 | 234 | 2 | 46 | 2073.66 | 480 | 513 | 105 | 36.7268 | 9.0858 | 0.81471 | 8.5013 | 1.8597
29 | 5 | 24 | 140 | 1.25 | 140 | 1 | 54 | 2803.64 | 540 | 666.9 | 160 | 41.451 | 9.8599 | 0.79837 | 7.9837 | 2.3656
30 | 5 | 24 | 115 | 0.51 | 197 | 2 | 51 | 2745.5 | 480 | 641.25 | 135 | 41.0982 | 9.5991 | 0.76343 | 7.1853 | 2.0209
31 | 5 | 24 | 124 | 6.72 | 142 | 1 | 55 | 2971.6 | 560 | 684 | 110 | 41.4793 | 9.5477 | 0.76772 | 7.8168 | 1.5354
TOTAL |  | 734.5 |  |  | 167054 | 29 | 1847 | 82817.2 | 15460 | 19152 | 2955
AVG | 4.7419 |  | 73.1613 | 1.0181 | 5388.8387 | 0.93548 | 59.5806 | 2547.5891 | 498.7097 | 572.0727 | 98.5 | 41.5609 | 9.8153 | 0.9506 | 7.9179 | 1.5593
MIN | 4 |  | 0 | 0 | 0 | 0 | 46 | 1963.84 | 140 | 470.25 | 47 | 36.7268 | 8.2676 | 0.76343 | 2.2442 | 0.74445
MAX | 5 |  | 140 | 6.72 | 164000 | 3 | 82 | 3998.74 | 960 | 666.9 | 160 | 48.9667 | 13.5427 | 1.1682 | 12.948 | 2.4731

## Monthly Chemical Report
Month, Year: |  | July/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #REF!
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 8.5 | 838.86 | 10.5598 | 89.758 | 5620.2 | 62.4834 | 531.1089 | 500 | 21.1471 | 179.75 | 666.9 | 57.2749 | 486.837 | [9 empty] | 95 | 23.4091 | 198.9775 | 280.5 | 174.8743 | 1766.9314
2 | 6.61 | 624.03 | 10.1015 | 66.7712 | 7997.48 | 114.3361 | 755.7619 | 520 | 28.2814 | 186.94 | 581.4 | 64.2091 | 424.422 | [9 empty] | 93 | 29.4688 | 194.7885 | 218.13 | 246.3969 | 1846.8136
3 | 7.39 | 736.56 | 10.6647 | 78.8119 | 5155.08 | 65.9208 | 487.1551 | 580 | 28.2152 | 208.51 | 624.15 | 61.6549 | 455.6295 | [9 empty] | 84 | 23.8076 | 175.938 | 243.87 | 190.2631 | 1649.9145
4 | 6.43 | 583.11 | 9.7034 | 62.3928 | 4379.88 | 64.3699 | 413.8987 | 480 | 26.8367 | 172.56 | 538.65 | 61.1531 | 393.2145 | [9 empty] | 64 | 20.8473 | 134.048 | 212.19 | 182.9104 | 1388.3039
5 | 7.22 | 470.58 | 6.974 | 50.3521 | 4909.6 | 64.26 | 463.9572 | 520 | 25.892 | 186.94 | 555.75 | 56.1908 | 405.6975 | [9 empty] | 81 | 23.4979 | 169.6545 | 238.26 | 176.8146 | 1514.8613
6 | 7.47 | 664.95 | 9.5247 | 71.1497 | 5245.52 | 66.359 | 495.7016 | 540 | 25.988 | 194.13 | 624.15 | 60.9946 | 455.6295 | [9 empty] | 63 | 17.6645 | 131.9535 | 246.51 | 180.5307 | 1595.0743
7 | 5.55 | 491.04 | 9.4669 | 52.5413 | 3927.68 | 66.8767 | 371.1658 | 460 | 29.7964 | 165.37 | 470.25 | 61.8527 | 343.2825 | [9 empty] | 55 | 20.7563 | 115.1975 | 183.15 | 188.749 | 1230.707
8 | 6.44 | 583.11 | 9.6883 | 62.3928 | 4509.08 | 66.1658 | 426.1081 | 460 | 25.6786 | 165.37 | 513 | 58.1506 | 374.49 | [9 empty] | 55 | 17.8878 | 115.1975 | 212.52 | 177.5712 | 1356.0783
9 | 7.48 | 675.18 | 9.6583 | 72.2443 | 5155.08 | 65.1277 | 487.1551 | 140 | 6.7286 | 50.33 | 581.4 | 56.7409 | 424.422 | [9 empty] | 67 | 18.7609 | 140.3315 | 246.84 | 157.0164 | 1421.3228
10 | 6.66 | 572.88 | 9.2039 | 61.2982 | 4625.36 | 65.6301 | 437.0965 | 260 | 14.0345 | 93.47 | 555.75 | 60.9155 | 405.6975 | [9 empty] | 78 | 24.5302 | 163.371 | 219.78 | 174.3143 | 1380.7132
11 | 6.59 | 562.65 | 9.1356 | 60.2035 | 4522 | 64.8451 | 427.329 | 320 | 17.4568 | 115.04 | 581.4 | 64.4039 | 424.422 | [9 empty] | 106 | 33.69 | 222.017 | 217.47 | 189.5313 | 1466.4816
12 | 7.08 | 593.34 | 8.9671 | 63.4874 | 4845 | 64.6684 | 457.8525 | 640 | 32.4972 | 230.08 | 555.75 | 57.3019 | 405.6975 | [9 empty] | 106 | 31.3583 | 222.017 | 233.64 | 194.793 | 1612.7744
13 | 7.57 | 644.49 | 9.1097 | 68.9604 | 5193.84 | 64.8372 | 490.8179 | 500 | 23.745 | 179.75 | 855 | 82.4505 | 624.15 | [9 empty] | 47 | 13.0042 | 98.4415 | 249.81 | 193.1466 | 1711.9298
14 | 7.93 | 664.95 | 8.9722 | 71.1497 | 5568.52 | 66.3588 | 526.2251 | 560 | 25.3871 | 201.32 | 837.9 | 77.1333 | 611.667 | [9 empty] | 109 | 28.7895 | 228.3005 | 261.69 | 206.6409 | 1900.3523
15 | 7.48 | 644.49 | 9.2193 | 68.9604 | 5180.92 | 65.4541 | 489.5969 | 540 | 25.9532 | 194.13 | 538.65 | 52.5688 | 393.2145 | [9 empty] | 92 | 25.7612 | 192.694 | 246.84 | 178.9567 | 1585.4359
16 | 8.48 | 705.87 | 8.9066 | 75.5281 | 5839.84 | 65.0784 | 551.8649 | 640 | 27.1321 | 230.08 | 709.65 | 61.0902 | 518.0445 | [9 empty] | 130 | 32.1091 | 272.285 | 279.84 | 194.3163 | 1927.6425
17 | 7.03 | 542.19 | 8.2524 | 58.0143 | 4909.6 | 65.9968 | 463.9572 | 400 | 20.4552 | 143.8 | 538.65 | 55.9338 | 393.2145 | [9 empty] | 145 | 43.2009 | 303.7025 | 231.99 | 193.8391 | 1594.6785
18 | 8.3 | 695.64 | 8.9679 | 74.4335 | 5723.56 | 65.1658 | 540.8764 | 560 | 24.2554 | 201.32 | 812.25 | 71.4389 | 592.9425 | [9 empty] | 110 | 27.7584 | 230.395 | 273.9 | 197.5864 | 1913.8674
19 | 7.58 | 624.03 | 8.8089 | 66.7712 | 5335.96 | 66.5235 | 504.2482 | 440 | 20.8681 | 158.18 | 555.75 | 53.5221 | 405.6975 | [9 empty] | 74 | 20.4476 | 154.993 | 250.14 | 170.1702 | 1540.0299
20 | 7.04 | 562.65 | 8.5516 | 60.2035 | 4806.24 | 64.5156 | 454.1897 | 380 | 19.4048 | 136.61 | 513 | 53.1946 | 374.49 | [9 empty] | 91 | 27.0738 | 190.5995 | 232.32 | 172.7404 | 1448.4127
21 | 8.02 | 613.8 | 8.1891 | 65.6766 | 5555.6 | 65.4619 | 525.0042 | 620 | 27.7918 | 222.89 | 624.15 | 56.8117 | 455.6295 | [9 empty] | 85 | 22.1986 | 178.0325 | 264.66 | 180.453 | 1711.8928
22 | 8 | 613.8 | 8.2096 | 65.6766 | 5555.6 | 65.6255 | 525.0042 | 510 | 22.9181 | 183.345 | 598.5 | 54.6131 | 436.905 | [9 empty] | 103 | 26.9667 | 215.7335 | 264 | 178.333 | 1690.6643
23 | 8.06 | 613.8 | 8.1485 | 65.6766 | 5529.76 | 64.834 | 522.5623 | 730 | 32.5602 | 262.435 | 555.75 | 50.3347 | 405.6975 | [9 empty] | 87 | 22.6081 | 182.2215 | 265.98 | 178.4855 | 1704.5729
24 | 7.96 | 593.34 | 7.9758 | 63.4874 | 5555.6 | 65.9553 | 525.0042 | 300 | 13.549 | 107.85 | 641.25 | 58.8081 | 468.1125 | [9 empty] | 110 | 28.9441 | 230.395 | 262.68 | 175.2323 | 1657.5291
25 | 8.08 | 572.88 | 7.5864 | 61.2982 | 5607.28 | 65.5802 | 529.888 | 470 | 20.9115 | 168.965 | 624.15 | 56.3898 | 455.6295 | [9 empty] | 137 | 35.5132 | 286.9465 | 266.64 | 185.9811 | 1769.3671
26 | 8.74 | 644.49 | 7.8902 | 68.9604 | 5930.28 | 64.1203 | 560.4115 | 370 | 15.2191 | 133.015 | 709.65 | 59.2728 | 518.0445 | [9 empty] | 138 | 33.0711 | 289.041 | 288.42 | 179.5735 | 1857.8924
27 | 8.89 | 654.72 | 7.8802 | 70.055 | 7261.04 | 77.1843 | 686.1683 | 960 | 38.8211 | 345.12 | 684 | 56.1665 | 499.32 | [9 empty] | 150 | 35.3403 | 314.175 | 293.37 | 215.3924 | 2208.2083
28 | 6.77 | 470.58 | 7.4375 | 50.3521 | 4147.32 | 57.891 | 391.9217 | 480 | 25.4889 | 172.56 | 513 | 55.3161 | 374.49 | [9 empty] | 105 | 32.4849 | 219.9225 | 223.41 | 178.6184 | 1432.6563
29 | 8.11 | 552.42 | 7.2884 | 59.1089 | 5607.28 | 65.3376 | 529.888 | 540 | 23.9371 | 194.13 | 666.9 | 60.0292 | 486.837 | [9 empty] | 160 | 41.3218 | 335.12 | 267.63 | 197.9142 | 1872.7139
30 | 8.01 | 521.73 | 6.9694 | 55.8251 | 5491 | 64.7815 | 518.8995 | 480 | 21.5431 | 172.56 | 641.25 | 58.441 | 468.1125 | [9 empty] | 135 | 35.3006 | 282.7575 | 264.33 | 187.0355 | 1762.4846
31 | 8.59 | 562.65 | 7.0086 | 60.2035 | 5943.2 | 65.3821 | 561.6324 | 560 | 23.4366 | 201.32 | 684 | 58.1281 | 499.32 | [9 empty] | 110 | 26.8213 | 230.395 | 283.47 | 180.7766 | 1836.341
Total | 234.06 |  |  | 2021.7447 |  |  | 15652.4508 |  |  | 5557.87 |  |  | 13980.96 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 6419.6425 | 7723.98 | 5778.9572 | 51356.648
Avg. | 7.5503 | 609.51 | 8.6781 | 65.2176 | 5343.0452 | 67.0041 | 504.9178 | 498.7097 | 23.7397 | 179.2861 | 617.8065 | 59.7576 | 450.9987 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 98.871 | 27.2385 | 207.0852 | 249.1606 | 219.4166 | 1656.6661
Max | 8.89 | 838.86 | 10.6647 | 89.758 | 7997.48 | 114.3361 | 755.7619 | 960 | 38.8211 | 345.12 | 855 | 82.4505 | 624.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 43.2009 | 335.12 | 293.37 | 246.3969 | 2208.2083
Min. | 5.55 | 470.58 | 6.9694 | 50.3521 | 3927.68 | 57.891 | 371.1658 | 140 | 6.7286 | 50.33 | 470.25 | 50.3347 | 343.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 13.0042 | 98.4415 | 183.15 | 157.0164 | 1230.707
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 2.0945 | Lime | 33 | Per MGD
|  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract |  | 0.21942 | PerKG

## LAS Meter
Month:
LAS Carrier Water Meter
Prev. | 2946040
1 | 2987190 | 41150
2 | 3028510 | 41320
3 | 3069700 | 41190
4 | 3109450 | 39750
5 | 3149990 | 40540
6 | 3191650 | 41660
7 | 3232740 | 41090
8 | 3273240 | 40500
9 | 3313920 | 40680
10 | 3355820 | 41900
11 | 3396310 | 40490
12 | 3437340 | 41030
13 | 3478110 | 40770
14 | 3519790 | 41680
15 | 3560760 | 40970
16 | 3601610 | 40850
17 | 3643440 | 41830
18 | 3683600 | 40160
19 | 3724820 | 41220
20 | 3765780 | 40960
21 | 3806920 | 41140
22 | 3847890 | 40970
23 | 3889170 | 41280
24 | 3930790 | 41620
25 | 3972200 | 41410
26 | 4012940 | 40740
27 | 4055230 | 42290
28 | 4096690 | 41460
29 | 4137850 | 41160
30 | 4178120 | 40270
31 | 4219440 | 41320
Total |  | 1273400

## Graphs
Chemicals | Amount
LAS | #REF!
Fe | 15652.4508
CL2 | 5557.87
Poly | 13980.96
Potassium | 6419.6425
Lime | 0
Chemfloc 3315 | 51356.648