## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: June 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 17712.88 |  | 9024388 |  | 37.3154 |  | 37406 |  | 8298632 |  | 188.9261 |  |  |  |  | 4621.46
1 | 17719.74 | 6.86 | 9024388 | 0 | 37.3155 | 0.0001 | 37406 | 0 | 8393742 | 0.09511 | 195.758 | 6.8319 | 733.77 | 26432 | 538.52 | 4624.78 | 3.32
2 | 17726.39 | 6.65 | 9201858 | 0.17747 | 37.3156 | 0.0001 | 37562 | 0.156 | 8492755 | 0.099013 | 202.3166 | 6.5586 | 733.74 | 26385 | 538.3 | 4628.08 | 3.3
3 | 17732.41 | 6.02 | 9201858 | 0 | 37.3483 | 0.0327 | 37562 | 0 | 8589599 | 0.096844 | 208.779 | 6.4624 | 733.71 | 26338 | 538.14 | 4629.52 | 1.44
4 | 17739.23 | 6.82 | 9416780 | 0.21492 | 37.3867 | 0.0384 | 37660 | 0.098 | 8685820 | 0.096221 | 215.6884 | 6.9094 | 733.68 | 26291 | 538.13 | 4631.71 | 2.19
5 | 17746.23 | 7 | 9659476 | 0.2427 | 37.4395 | 0.0528 | 37909 | 0.249 | 8783007 | 0.097187 | 222.7682 | 7.0798 | 733.67 | 26275 | 538.11 | 4635.44 | 3.73
6 | 17753.29 | 7.06 | 9873028 | 0.21355 | 37.4397 | 0.0002 | 38015 | 0.106 | 8880797 | 0.09779 | 229.9683 | 7.2001 | 733.65 | 26266 | 530.09 | 4639.17 | 3.73
7 | 17760.46 | 7.17 | 9945396 | 0.072368 | 37.4478 | 0.0081 | 38015 | 0 | 8978381 | 0.097584 | 236.97 | 7.0017 | 733.62 | 26196 | 538.06 | 4642.9 | 3.73
8 | 17767.81 | 7.35 | 10122458.2 | 0.17706 | 37.5095 | 0.0617 | 38115 | 0.1 | 9076190 | 0.097809 | 244.3404 | 7.3704 | 733.6 | 26165 | 538.03 | 4646.67 | 3.77
9 | 17774.88 | 7.07 | 10298910 | 0.17645 | 37.5772 | 0.0677 | 38351 | 0.236 | 9175653 | 0.099463 | 251.5679 | 7.2275 | 733.57 | 26118 | 538 | 4650.34 | 3.67
10 | 17782.11 | 7.23 | 10587494 | 0.28858 | 37.6304 | 0.0532 | 38557 | 0.206 | 9276254 | 0.1006 | 259.1244 | 7.5565 | 733.52 | 26040 | 537.96 | 4654.11 | 3.77
11 | 17789.66 | 7.55 | 10700172 | 0.11268 | 37.6304 | 0 | 38557 | 0 | 9378508 | 0.10225 | 266.7925 | 7.6681 | 733.48 | 25977 | 537.92 | 4657.82 | 3.71
12 | 17797.5 | 7.84 | 10892538 | 0.19237 | 37.6869 | 0.0565 | 38692 | 0.135 | 9481664 | 0.10316 | 274.2232 | 7.4307 | 733.45 | 25930 | 537.88 | 4661.54 | 3.72
13 | 17805.1 | 7.6 | 11049287 | 0.15675 | 37.7159 | 0.029 | 38785 | 0.093 | 9583638 | 0.10197 | 281.9528 | 7.7296 | 733.42 | 25883 | 537.85 | 4665.27 | 3.73
14 | 17812.67 | 7.57 | 11348329 | 0.29904 | 37.775 | 0.0591 | 39087 | 0.302 | 9686197 | 0.10256 | 290.0957 | 8.1429 | 733.39 | 25836 | 537.81 | 4669.01 | 3.74
15 | 17820.14 | 7.47 | 11417466 | 0.069137 | 37.775 | 0 | 39087 | 0 | 9787109 | 0.10091 | 297.5359 | 7.4402 | 733.36 | 25790 | 537.78 | 4672.74 | 3.73
16 | 17827.71 | 7.57 | 11570401 | 0.15293 | 37.775 | 0 | 39163 | 0.076 | 9890606 | 0.1035 | 305.2941 | 7.7582 | 733.33 | 25743 | 537.74 | 4676.52 | 3.78
17 | 17835.72 | 8.01 | 11667601 | 0.0972 | 37.8539 | 0.0789 | 39264 | 0.101 | 9990704 | 0.1001 | 313.2767 | 7.9826 | 733.29 | 25680 | 537.7 | 4680.19 | 3.67
18 | 17844.14 | 8.42 | 11870155 | 0.20255 | 37.8835 | 0.0296 | 39354 | 0.09 | 10094680 | 0.10398 | 321.4762 | 8.1995 | 733.25 | 25618 | 537.66 | 4683.53 | 3.34
19 | 17851.48 | 7.34 | 12002874 | 0.13272 | 37.9398 | 0.0563 | 39407 | 0.053 | 10197059 | 0.10238 | 329.1932 | 7.717 | 733.22 | 25571 | 537.62 | 4687 | 3.47
20 | 17859.07 | 7.59 | 12302894 | 0.30002 | 37.9918 | 0.052 | 39655 | 0.248 | 10300100 | 0.10304 | 336.8485 | 7.6553 | 733.52 | 26040 | 537.65 | 4687.57 | 0.57
21 | 17866.45 | 7.38 | 12378190 | 0.075296 | 37.9919 | 0.0001 | 39736 | 0.081 | 10401038 | 0.10094 | 344.4123 | 7.5638 | 733.64 | 26228 | 537.63 | 4687.57 | 0
22 | 17873.84 | 7.39 | 12501493 | 0.1233 | 37.9919 | 0 | 39849 | 0.113 | 10506959 | 0.10592 | 352.353 | 7.9407 | 733.63 | 26212 | 537.63 | 4687.57 | 0
23 | 17881.42 | 7.58 | 12679697 | 0.1782 | 38.0626 | 0.0707 | 39950 | 0.101 | 10609854 | 0.1029 | 359.6257 | 7.2727 | 733.82 | 26511 | 537.65 | 4688.36 | 0.79
24 | 17888.32 | 6.9 | 12933015 | 0.25332 | 38.0626 | 0 | 40073 | 0.123 | 10705238 | 0.095384 | 366.42 | 6.7943 | 734 | 26795 | 537.61 | 4691.79 | 3.43
25 | 17894.2 | 5.88 | 13012448 | 0.079433 | 38.1019 | 0.0393 | 40170 | 0.097 | 10803816 | 0.098578 | 372.897 | 6.477 | 733.98 | 26763 | 537.66 | 4695.35 | 3.56
26 | 17901.48 | 7.28 | 13254329 | 0.24188 | 38.1271 | 0.0252 | 40333 | 0.163 | 10916742 | 0.11293 | 379.8096 | 6.9126 | 733.85 | 26558 | 537.6 | 4698.89 | 3.54
27 | 17908.22 | 6.74 | 13483914 | 0.22959 | 38.1947 | 0.0676 | 40451 | 0.118 | 11019449 | 0.10271 | 386.6195 | 6.8099 | 733.82 | 26511 | 522.58 | 4702.36 | 3.47
28 | 17914.63 | 6.41 | 13679900 | 0.19599 | 38.1948 | 0.0001 | 40755 | 0.304 | 11118091 | 0.098642 | 393.479 | 6.8595 | 733.78 | 26448 | 537.55 | 4705.84 | 3.48
29 | 17921.05 | 6.42 | 13919245 | 0.23935 | 38.2358 | 0.041 | 40880 | 0.125 | 11218564 | 0.10047 | 399.9957 | 6.5167 | 733.74 | 26385 | 537.51 | 4709.32 | 3.48
30 | 17926.98 | 5.93 | 14063086 | 0.14384 | 38.2768 | 0.041 | 40880 | 0 | 11337967 | 0.1194 | 406.5215 | 6.5258 | 733.71 | 26338 | 537.49 | 4712.88 | 3.56
31
Totals | 534722.33 | 214.1 |  | 5.0387 |  | 0.9614 |  | 3.474 |  | 3.0393 |  | 217.5954 |  |  |  |  | 91.42
Average | 17824.0777 | 7.1367 |  | 0.16796 |  | 0.032047 |  | 0.1158 |  | 0.10131 |  | 7.2532 | 733.607 |  | 537.062 |  | 3.0473
Min |  | 5.88 |  | 0 |  | 0 |  | 0 |  | 0.09511 |  | 6.4624 | 733.22 |  | 522.58 |  | 0
Max |  | 8.42 |  | 0.30002 |  | 0.0789 |  | 0.304 |  | 0.1194 |  | 8.1995 | 734 |  | 538.52 |  | 3.78
Calculated Values
| Raw Water Added To System (MG) |  |  | 209.0613 |  |  | Raw to Potable Differential |  |  | -2.0208
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 211.0821 |  |  | Average Raw for Month |  |  | 7.1367
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.6033 |  |  | Peak Raw Flow for Month |  |  | 8.42
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | June/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 70 | 0 | 23.5 | 6.26 | 2.5467 | 0.12233 | 8.43 | 8.7883 | 3.7017 | 103 | 135.3333 | 139 | 67.6667 | 7
2 | 75 | 0 | 22.5 | 5.6 | 2.7667 | 0.1075 | 8.16 | 8.6883 | 3.7058 | 131 | 134.6667 | 119 | 78 | 7.6667
3 | 72 | 0 | 23.1667 | 8.22 | 2.1433 | 0.096167 | 8.56 | 8.83 | 3.705 | 138 | 133.3333 | 127 | 69.6667 | 9
4 | 79 | 0 | 22.5 | 5.94 | 2.44 | 0.10717 | 8.61 | 8.8217 | 3.56 | 140 | 129.6667 | 120 | 63.6667 | 8.3333
5 | 91 | 0 | 24.3333 | 6.36 | 2.2533 | 0.10933 | 8.4 | 8.8183 | 3.5433 | 143 | 122 | 100 | 60.3333 | 7
6 | 71 | 0 | 24.5 | 5.54 | 1.8683 | 0.10183 | 8.65 | 8.9383 | 3.7775 | 152 | 117.3333 | 117 | 64 | 9.6667
7 | 83 | 0 | 24.8333 | 6.13 | 2.29 | 0.086833 | 8.57 | 8.8417 | 3.5992 | 140 | 124.3333 | 108 | 74 | 5.3333
8 | 83 | 0 | 25.5 | 6.72 | 2.505 | 0.0905 | 8.77 | 8.7983 | 3.6992 | 129 | 141 | 100 | 81.3333 | 6.6667
9 | 79 | 0 | 24.8333 | 8.04 | 2.5067 | 0.1425 | 8.65 | 8.5283 | 3.3483 | 126 | 139 | 98 | 59.1667 | 11.6667
10 | 63 | 0 | 25.3333 | 10.4 | 2.735 | 0.12283 | 8.64 | 8.7833 | 3.3783 | 124 | 135.6667 | 99 | 79.6667 | 5.3333
11 | 90 | 0 | 24.6667 | 9.81 | 2.7733 | 0.1105 | 8.67 | 8.7133 | 3.1858 | 130 | 142 | 108 | 82.3333 | 3
12 | 72 | 0 | 24 | 6.3 | 3.2567 | 0.107 | 8.45 | 8.7033 | 3.2675 | 140 | 132.3333 | 103 | 77 | 4.6667
13 | 78 | 0 | 23.8333 | 7.07 | 3.0617 | 0.12133 | 8.44 | 8.7867 | 3.3808 | 147 | 130 | 108 | 77.6667 | 4.6667
14 | 75 | 0 | 23.5 | 7.8 | 2.5917 | 0.11967 | 8.53 | 8.875 | 3.555 | 128 | 131.6667 | 103 | 71 | 8.3333
15 | 81 | 0 | 24.1667 | 7.85 | 2.4417 | 0.14483 | 8.55 | 8.6017 | 3.245 | 140 | 139 | 100 | 79.3333 | 3.6667
16 | 76 | 0 | 24.5 | 7.06 | 2.2117 | 0.097833 | 8.53 | 9.065 | 3.6433 | 126 | 134 | 102 | 60 | 7.3333
17 | 75 | 0 | 24.1667 | 7.51 | 2.4633 | 0.087333 | 8.56 | 9.035 | 3.7342 | 135 | 120 | 110 | 64 | 6
18 | 81 | 0 | 23.8333 | 11.8 | 2.6117 | 0.10414 | 8.53 | 8.94 | 3.8092 | 138 | 144.3333 | 113 | 77.3333 | 7
19 | 67 | 2 | 24.1667 | 16.2 | 2.63 | 0.091 | 8.32 | 8.9917 | 3.6692 | 135 | 132.3333 | 116 | 73 | 5
20 | 81 | 0 | 25.5 | 20.2 | 2.4017 | 0.10583 | 8.41 | 9.0467 | 3.5967 | 130 | 114 | 108 | 62.6667 | 7
21 | 78 | 0 | 24.1667 | 20.2 | 2.4433 | 0.10717 | 8.15 | 8.89 | 3.4608 | 136 | 130.6667 | 111 | 71.6667 | 8.6667
22 | 79 | 0.2 | 23.6667 | 5.81 | 2.5183 | 0.083667 | 8.15 | 8.885 | 3.4458 | 140 | 122 | 120 | 70.3333 | 7.6667
23 | 72 | 0 | 24 | 7.02 | 2.3567 | 0.077833 | 8.32 | 9.0183 | 3.3375 | 149 | 112.6667 | 110 | 60.3333 | 3.3333
24 | 78 | 0 | 25.6667 | 10.2 | 2.635 | 0.1005 | 8.32 | 9.05 | 3.1308 | 130 | 111.6667 | 100 | 56.6667 | 5.6667
25 | 73 | 0 | 25 | 8.48 | 2.475 | 0.085333 | 8.55 | 8.835 | 2.8117 | 132 | 127.3333 | 100 | 69.3333 | 8.3333
26 | 75 | 0 | 25 | 8.44 | 2.3117 | 0.10033 | 8.18 | 8.9117 | 3.2558 | 135 | 126.3333 | 107 | 68.3333 | 10.6667
27 | 76 | 0 | 24.5 | 8.25 | 1.9133 | 0.102 | 8.23 | 8.9217 | 3.2433 | 136 | 126.3333 | 108 | 69 | 9.6667
28 | 80 | 0 | 24.5 | 9.38 | 2.0667 | 0.11417 | 8.46 | 8.9767 | 3.245 | 140 | 124 | 105 | 63.3333 | 6.6667
29 | 84 | 0 | 25.3333 | 10.8 | 1.9583 | 0.099167 | 8.48 | 8.9967 | 3.1142 | 135 | 132 | 112 | 56.3333 | 6.3333
30 | 81 | 0 | 25.1667 | 9.25 | 1.865 | 0.092167 | 8.44 | 8.94 | 3.0433 | 136 | 124.3333 | 100 | 58 | 4.6667
31 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
TOTAL |  | 2.2
AVG. | 74.7742 | 0.070968 | 24.3444 | 8.9547 | 2.4347 | 0.10463 | 8.457 | 8.8673 | 3.4398 | 134.8 | 128.9778 | 109.0333 | 68.8389 | 6.8667
MAX. | 91 | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MIN. | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: June 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 5 | 24 | 0 | 0 | 0 | 0 | 59 | 2377.28 | 400 | 555.75 | 72 | 41.5518 | 9.7138 | 1.0312 | 6.9915 | 1.2585
2 | 5 | 24 | 86 | 0.67 | 156 | 1 | 56 | 2319.14 | 400 | 555.75 | 50 | 41.8157 | 10.0206 | 1.0097 | 7.2123 | 0.90153
3 | 5 | 24 | 0 | 0 | 0 | 0 | 50 | 2125.34 | 300 | 367.65 | 41 | 42.3317 | 7.3227 | 0.99588 | 5.9753 | 0.81662
4 | 5 | 24 | 119 | 1.23 | 109 | 1 | 58 | 2338.52 | 360 | 555.75 | 53 | 41.1141 | 9.7708 | 1.0197 | 6.3292 | 0.93181
5 | 7 | 24 | 116 | 0.855 | 249 | 2 | 60 | 2396.66 | 380 | 624.15 | 70 | 41.0528 | 10.6912 | 1.0277 | 6.5091 | 1.199
6 | 7 | 24 | 122 | 5.97 | 106 | 1 | 58 | 2403.12 | 260 | 581.4 | 69 | 40.8136 | 9.8743 | 0.98505 | 4.4157 | 1.1719
7 | 7 | 24 | 0 | 0 | 0 | 0 | 59 | 2448.34 | 380 | 555.75 | 74 | 40.9436 | 9.2938 | 0.98666 | 6.3547 | 1.2375
8 | 5 | 24 | 95 | 0.95 | 100 | 1 | 62 | 2545.24 | 400 | 470.25 | 73 | 41.5217 | 7.6714 | 1.0114 | 6.5254 | 1.1909
9 | 5 | 24 | 107 | 0.73 | 236 | 2 | 56 | 2390.2 | 380 | 581.4 | 78 | 40.5367 | 9.8603 | 0.94974 | 6.4446 | 1.3228
10 | 5 | 24 | 112 | 0.59 | 206 | 2 | 53 | 2480.64 | 400 | 581.4 | 81 | 41.1395 | 9.6421 | 0.87896 | 6.6337 | 1.3433
11 | 5 | 24 | 0 | 0 | 0 | 0 | 55 | 2577.54 | 440 | 795.15 | 77 | 40.9348 | 12.628 | 0.87347 | 6.9878 | 1.2229
12 | 6 | 24 | 114 | 8.73 | 135 | 1 | 60 | 2764.88 | 380 | 624.15 | 69 | 42.2858 | 9.5457 | 0.91763 | 5.8117 | 1.0553
13 | 5 | 24 | 120 | 0.47 | 93 | 1 | 58 | 2558.16 | 460 | 1068.75 | 103 | 40.3597 | 16.8615 | 0.91506 | 7.2574 | 1.625
14 | 5 | 24 | 103 | 1.92 | 302 | 2 | 57 | 2629.22 | 360 | 598.5 | 110 | 41.6452 | 9.4799 | 0.90284 | 5.7022 | 1.7423
15 | 5 | 24 | 109 | 0.96 | 112 | 1 | 58 | 2584 | 620 | 581.4 | 78 | 41.4769 | 9.3323 | 0.93098 | 9.9519 | 1.252
16 | 5 | 24 | 123 | 0.51 | 76 | 1 | 61 | 2609.84 | 570 | 581.4 | 100 | 41.3382 | 9.209 | 0.9662 | 9.0284 | 1.5839
17 | 5 | 24 | 105 | 0.48 | 71 | 1 | 65 | 2758.42 | 510 | 641.25 | 54 | 41.2916 | 9.5991 | 0.973 | 7.6343 | 0.80834
18 | 5 | 24 | 120 | 1.44 | 90 | 1 | 66 | 2939.3 | 500 | 666.9 | 67 | 41.8568 | 9.4969 | 0.93987 | 7.1202 | 0.95411
19 | 5 | 24 | 110 | 3.48 | 53 | 1 | 59 | 2584 | 480 | 555.75 | 110 | 42.2115 | 9.0786 | 0.96381 | 7.8411 | 1.7969
20 | 5 | 24 | 119 | 2.17 | 248 | 2 | 55 | 2590.46 | 360 | 624.15 | 110 | 40.9232 | 9.8601 | 0.86887 | 5.6871 | 1.7377
21 | 5 | 24 | 97 | 0.96 | 81 | 1 | 58 | 2584 | 340 | 538.65 | 115 | 41.9827 | 8.7515 | 0.94234 | 5.524 | 1.8684
22 | 4 | 24 | 97 | 0.54 | 103 | 1 | 58 | 2571.08 | 440 | 666.9 | 68 | 41.7162 | 10.8206 | 0.94106 | 7.1391 | 1.1033
23 | 4 | 24 | 108 | 0.51 | 101 | 1 | 60 | 2596.92 | 480 | 598.5 | 126 | 41.0793 | 9.4674 | 0.94911 | 7.5929 | 1.9931
24 | 5 | 20 | 99.5 | 1 | 224 | 2 | 53 | 2422.5 | 440 | 513 | 86 | 42.0968 | 8.9146 | 0.921 | 7.6461 | 1.4945
25 | 5 | 19 | 106 | 0.72 | 103 | 1 | 50 | 1957.38 | 560 | 453.15 | 75 | 39.9146 | 9.2406 | 1.0196 | 11.4194 | 1.5294
26 | 5 | 23 | 116 | 0.48 | 163 | 1 | 64 | 2551.7 | 560 | 598.5 | 65 | 42.0274 | 9.8575 | 1.0541 | 9.2234 | 1.0706
27 | 4 | 24 | 94 | 0.96 | 118 | 1 | 58 | 2584 | 580 | 513 | 65 | 45.9692 | 9.1262 | 1.0318 | 10.3182 | 1.1563
28 | 4 | 24 | 117 | 1.9 | 152 | 2 | 54 | 2273.92 | 480 | 513 | 70 | 42.5355 | 9.5961 | 1.0101 | 8.9788 | 1.3094
29 | 4 | 24 | 106 | 0.48 | 125 | 1 | 56 | 2286.84 | 430 | 538.65 | 60 | 42.7105 | 10.0602 | 1.0459 | 8.031 | 1.1206
30 | 5 | 24 | 0 | 0 | 0 | 0 | 56 | 2021.98 | 510 | 495.9 | 65 | 40.8843 | 10.0271 | 1.1323 | 10.3122 | 1.3143
31 | [6 empty] | 0 | 0 | 0 |  | 0 | #VALUE! | #VALUE! | 0 | 0 | 0
TOTAL |  | 710 |  |  | 3512 | 32 | 1732 | 74270.62 | 13160 | 17595.9 | 2334
AVG | 5.0667 |  | 90.6833 | 1.2902 | 117.0667 | 1.0667 | 55.871 | 2400.1836 | 424.5161 | 565.8545 | 77.8 | 41.762 | 9.8271 | 0.94178 | 7.1806 | 1.2617
MIN | 4 |  | 0 | 0 | 0 | 0 | 0 | 2125.34 | 0 | 367.65 | 41 | 39.9146 | #VALUE! | 0 | 0 | 0
MAX | 7 |  | 123 | 8.73 | 302 | 2 | 66 | 2577.54 | 620 | 795.15 | 126 | 45.9692 | #VALUE! | 1.1323 | 11.4194 | 1.9931

## Monthly Chemical Report
Month, Year: |  | June/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #REF!
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 6.86 | 603.57 | 9.4143 | 64.582 | 4754.56 | 65.4965 | 449.3059 | 400 | 20.9621 | 143.8 | 555.75 | 59.1396 | 405.6975 | [9 empty] | 72 | 21.9831 | 150.804 | 226.38 | 176.9955 | 1440.5694
2 | 6.65 | 572.88 | 9.2178 | 61.2982 | 4638.28 | 65.9124 | 438.3175 | 400 | 21.6241 | 143.8 | 555.75 | 61.0071 | 405.6975 | [9 empty] | 50 | 15.7481 | 104.725 | 219.45 | 173.5095 | 1373.2881
3 | 6.02 | 511.5 | 9.0914 | 54.7305 | 4250.68 | 66.7258 | 401.6893 | 300 | 17.9153 | 107.85 | 367.65 | 44.5821 | 268.3845 | [9 empty] | 41 | 14.2649 | 85.8745 | 198.66 | 152.5795 | 1117.1888
4 | 6.82 | 593.34 | 9.309 | 63.4874 | 4677.04 | 64.8065 | 441.9803 | 360 | 18.9765 | 129.42 | 555.75 | 59.4864 | 405.6975 | [9 empty] | 53 | 16.2769 | 111.0085 | 225.06 | 168.8554 | 1376.6537
5 | 7 | 613.8 | 9.3824 | 65.6766 | 4793.32 | 64.7098 | 452.9687 | 380 | 19.5157 | 136.61 | 624.15 | 65.0899 | 455.6295 | [9 empty] | 70 | 20.945 | 146.615 | 231 | 179.6428 | 1488.4998
6 | 7.06 | 593.34 | 8.9925 | 63.4874 | 4806.24 | 64.3328 | 454.1897 | 260 | 13.2394 | 93.47 | 581.4 | 60.1164 | 424.422 | [9 empty] | 69 | 20.4703 | 144.5205 | 232.98 | 167.1515 | 1413.0696
7 | 7.17 | 603.57 | 9.0073 | 64.582 | 4896.68 | 64.5378 | 462.7363 | 380 | 19.053 | 136.61 | 555.75 | 56.5826 | 405.6975 | [9 empty] | 74 | 21.6169 | 154.993 | 236.61 | 170.7976 | 1461.2287
8 | 7.35 | 634.26 | 9.2334 | 67.8658 | 5090.48 | 65.449 | 481.0504 | 400 | 19.5646 | 143.8 | 470.25 | 46.7051 | 343.2825 | [9 empty] | 73 | 20.8025 | 152.8985 | 242.55 | 161.7547 | 1431.4472
9 | 7.07 | 572.88 | 8.6702 | 61.2982 | 4780.4 | 63.8964 | 451.7478 | 380 | 19.3225 | 136.61 | 581.4 | 60.0314 | 424.422 | [9 empty] | 78 | 23.1076 | 163.371 | 233.31 | 175.0281 | 1470.759
10 | 7.23 | 542.19 | 8.0241 | 58.0143 | 4961.28 | 64.8466 | 468.841 | 400 | 19.8893 | 143.8 | 581.4 | 58.7029 | 424.422 | [9 empty] | 81 | 23.4654 | 169.6545 | 238.59 | 174.9283 | 1503.3218
11 | 7.55 | 562.65 | 7.974 | 60.2035 | 5155.08 | 64.5238 | 487.1551 | 440 | 20.951 | 158.18 | 795.15 | 76.8821 | 580.4595 | [9 empty] | 77 | 21.3611 | 161.2765 | 249.15 | 191.692 | 1696.4246
12 | 7.84 | 613.8 | 8.3771 | 65.6766 | 5529.76 | 66.6534 | 522.5623 | 380 | 17.4247 | 136.61 | 624.15 | 58.116 | 455.6295 | [9 empty] | 69 | 18.4337 | 144.5205 | 258.72 | 169.005 | 1583.7189
13 | 7.6 | 593.34 | 8.3536 | 63.4874 | 5116.32 | 63.6174 | 483.4922 | 460 | 21.7592 | 165.37 | 1068.75 | 102.6563 | 780.1875 | [9 empty] | 103 | 28.386 | 215.7335 | 250.8 | 224.7725 | 1959.0706
14 | 7.57 | 583.11 | 8.2421 | 62.3928 | 5258.44 | 65.6437 | 496.9226 | 360 | 17.0964 | 129.42 | 598.5 | 57.7153 | 436.905 | [9 empty] | 110 | 30.4353 | 230.395 | 249.81 | 179.1328 | 1605.8453
15 | 7.47 | 593.34 | 8.499 | 63.4874 | 5168 | 65.3783 | 488.376 | 620 | 29.838 | 222.89 | 581.4 | 56.8169 | 424.422 | [9 empty] | 78 | 21.8703 | 163.371 | 246.51 | 182.4025 | 1609.0564
16 | 7.57 | 624.03 | 8.8205 | 66.7712 | 5219.68 | 65.1598 | 493.2598 | 570 | 27.0694 | 204.915 | 581.4 | 56.0663 | 424.422 | [9 empty] | 100 | 27.6684 | 209.45 | 249.81 | 184.7844 | 1648.628
17 | 8.01 | 664.95 | 8.8826 | 71.1497 | 5516.84 | 65.0863 | 521.3414 | 510 | 22.8895 | 183.345 | 641.25 | 58.441 | 468.1125 | [9 empty] | 54 | 14.1202 | 113.103 | 264.33 | 169.4197 | 1621.3815
18 | 8.42 | 675.18 | 8.5801 | 72.2443 | 5878.6 | 65.9772 | 555.5277 | 500 | 21.348 | 179.75 | 666.9 | 57.8191 | 486.837 | [9 empty] | 67 | 16.6664 | 140.3315 | 277.86 | 170.3908 | 1712.5505
19 | 7.34 | 603.57 | 8.7986 | 64.582 | 5168 | 66.5362 | 488.376 | 480 | 23.5095 | 172.56 | 555.75 | 55.2721 | 405.6975 | [9 empty] | 110 | 31.389 | 230.395 | 242.22 | 185.5055 | 1603.8305
20 | 7.59 | 562.65 | 7.932 | 60.2035 | 5180.92 | 64.5055 | 489.5969 | 360 | 17.0514 | 129.42 | 624.15 | 60.0302 | 455.6295 | [9 empty] | 110 | 30.3551 | 230.395 | 250.47 | 179.8742 | 1615.715
21 | 7.38 | 593.34 | 8.6026 | 63.4874 | 5168 | 66.1756 | 488.376 | 340 | 16.5623 | 122.23 | 538.65 | 53.2811 | 393.2145 | [9 empty] | 115 | 32.6379 | 240.8675 | 243.54 | 177.2595 | 1551.7154
22 | 7.39 | 593.34 | 8.591 | 63.4874 | 5142.16 | 65.7556 | 485.9341 | 440 | 21.4046 | 158.18 | 666.9 | 65.8778 | 486.837 | [9 empty] | 68 | 19.2728 | 142.426 | 243.87 | 180.9018 | 1580.7345
23 | 7.58 | 613.8 | 8.6645 | 65.6766 | 5193.84 | 64.7517 | 490.8179 | 480 | 22.7652 | 172.56 | 598.5 | 57.6392 | 436.905 | [9 empty] | 126 | 34.8162 | 263.907 | 250.14 | 188.6367 | 1680.0065
24 | 6.9 | 542.19 | 8.4079 | 58.0143 | 4845 | 66.3554 | 457.8525 | 440 | 22.9246 | 158.18 | 513 | 54.2739 | 374.49 | [9 empty] | 86 | 26.1054 | 180.127 | 227.7 | 178.0672 | 1456.3638
25 | 5.88 | 511.5 | 9.3079 | 54.7305 | 3914.76 | 62.9158 | 369.9448 | 560 | 34.2381 | 201.32 | 453.15 | 56.2584 | 330.7995 | [9 empty] | 75 | 26.7156 | 157.0875 | 194.04 | 189.4358 | 1307.9223
26 | 7.28 | 654.72 | 9.6229 | 70.055 | 5103.4 | 66.2461 | 482.2713 | 560 | 27.6538 | 201.32 | 598.5 | 60.0144 | 436.905 | [9 empty] | 65 | 18.7009 | 136.1425 | 240.24 | 182.2382 | 1566.9338
27 | 6.74 | 593.34 | 9.4195 | 63.4874 | 5168 | 72.4593 | 488.376 | 580 | 30.9362 | 208.51 | 513 | 55.5623 | 374.49 | [9 empty] | 65 | 20.1992 | 136.1425 | 222.42 | 188.5765 | 1493.4259
28 | 6.41 | 552.42 | 9.2214 | 59.1089 | 4547.84 | 67.0469 | 429.7709 | 480 | 26.9204 | 172.56 | 513 | 58.4228 | 374.49 | [9 empty] | 70 | 22.8729 | 146.615 | 211.53 | 184.4844 | 1394.0748
29 | 6.42 | 572.88 | 9.548 | 61.2982 | 4573.68 | 67.3229 | 432.2128 | 430 | 24.0787 | 154.585 | 538.65 | 61.2484 | 393.2145 | [9 empty] | 60 | 19.5748 | 125.67 | 211.86 | 181.7727 | 1378.8404
30 | 5.93 | 572.88 | 10.337 | 61.2982 | 4043.96 | 64.4442 | 382.1542 | 510 | 30.9182 | 183.345 | 495.9 | 61.0467 | 362.007 | [9 empty] | 65 | 22.9583 | 136.1425 | 195.69 | 189.7044 | 1320.6369
31 |  | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 |  | #VALUE! | #VALUE! | [9 empty] | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE!
Total | 214.1 |  |  | 1895.8645 |  |  | 14037.1472 |  |  | 4731.02 |  |  | #VALUE! |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 4888.563 | 7065.3 | 5379.2995 | 45462.9017
Avg. | 7.1367 | 571.56 | 8.8842 | 61.1569 | 4791.6529 | 65.5756 | 452.8112 | 424.5161 | 22.2467 | 152.6135 | 586.53 | 59.8295 | 428.1669 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 75.2903 | 22.774 | 157.6956 | 235.51 | 212.3442 | 1515.4301
Max | 8.42 | 675.18 | #VALUE! | 72.2443 | 5878.6 | #VALUE! | 555.5277 | 620 | #VALUE! | 222.89 | 1068.75 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | #VALUE! | 263.907 | #VALUE! | #VALUE! | #VALUE!
Min. | 5.88 | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 | 0 | #VALUE! | 0 | 367.65 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE!
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 2.0945 | Lime | 33 | Per MGD
|  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract |  | 0.21234 | PerKG

## LAS Meter
Month:
LAS Carrier Water Meter
Prev.
1 | 1760900 | 1760900
2 | 1801820 | 40920
3 | 1842660 | 40840
4 | 1882580 | 39920
5 | 1922870 | 40290
6 | 1963710 | 40840
7 | 2004250 | 40540
8 | 2045380 | 41130
9 | 2085860 | 40480
10 | 2126710 | 40850
11 | 2167160 | 40450
12 | 2207740 | 40580
13 | 2248340 | 40600
14 | 2289680 | 41340
15 | 2330960 | 41280
16 | 2372050 | 41090
17 | 2412570 | 40520
18 | 2454210 | 41640
19 | 2494960 | 40750
20 | 2536410 | 41450
21 | 2577630 | 41220
22 | 2618650 | 41020
23 | 2659960 | 41310
24 | 2698860 | 38900
25 | 2740650 | 41790
26 | 2782260 | 41610
27 | 2823170 | 40910
28 | 2863810 | 40640
29 | 2904690 | 40880
30 | 2946040 | 41350
31 | 0 | -2946040
Total |  | 0

## Graphs
Chemicals | Amount
LAS | 2021.7447
Fe | 14037.1472
CL2 | 4731.02
Poly | #VALUE!
Potassium | 4888.563
Lime | 0
Chemfloc 3315 | 45462.9017