## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: May 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 17535.32 |  | 4223689 |  | 36.5908 |  | 34200 |  | 5345935 |  | 8.9429 |  |  |  |  | 4514.89
1 | 17541.61 | 6.29 | 4374711 | 0.15102 | 36.5909 | 0.0001 | 34283 | 0.083 | 5445470 | 0.099535 | 15.1126 | 6.1697 | 733.9 | 26637 | 537.96 | 4516.89 | 2
2 | 17547.58 | 5.97 | 4623808 | 0.2491 | 36.6342 | 0.0433 | 34595 | 0.312 | 5542181 | 0.096711 | 21.0165 | 5.9039 | 733.85 | 26558 | 537.87 | 4520.62 | 3.73
3 | 17552.89 | 5.31 | 4774060 | 0.15025 | 36.6962 | 0.062 | 34595 | 0 | 5638560 | 0.096379 | 26.5138 | 5.4973 | 733.81 | 26511 | 537.81 | 4524.34 | 3.72
4 | 17558.88 | 5.99 | 4786990 | 0.01293 | 36.6963 | 0.0001 | 34595 | 0 | 5739072 | 0.10051 | 32.6179 | 6.1041 | 733.79 | 26464 | 537.73 | 4528.1 | 3.76
5 | 17565.02 | 6.14 | 4876033 | 0.089043 | 36.6964 | 0.0001 | 34668 | 0.073 | 5839975 | 0.1009 | 38.7195 | 6.1016 | 733.77 | 26432 | 537.7 | 4531.91 | 3.81
6 | 17570.9 | 5.88 | 4876033 | 0 | 36.6964 | 0 | 34770 | 0.102 | 5938200 | 0.098225 | 44.6377 | 5.9182 | 733.73 | 26369 | 537.61 | 4535.6 | 3.69
7 | 17577.08 | 6.18 | 5130032 | 0.254 | 36.6965 | 0.0001 | 34898 | 0.128 | 6038058 | 0.099858 | 50.7357 | 6.098 | 733.7 | 26322 | 537.56 | 4539.41 | 3.81
8 | 17582.02 | 4.94 | 5379889 | 0.24986 | 36.7789 | 0.0824 | 35119 | 0.221 | 6135551 | 0.097493 | 56.037 | 5.3013 | 733.68 | 26291 | 537.55 | 4543.18 | 3.77
9 | 17586.98 | 4.96 | 5463314 | 0.083425 | 36.779 | 0.0001 | 35119 | 0 | 6229141 | 0.09359 | 61.3122 | 5.2752 | 733.66 | 26259 | 537.51 | 4546.89 | 3.71
10 | 17592.13 | 5.15 | 5563787 | 0.10047 | 36.7791 | 0.0001 | 35252 | 0.133 | 6324014 | 0.094873 | 66.8606 | 5.5484 | 733.64 | 26220 | 537.48 | 4550.65 | 3.76
11 | 17598.36 | 6.23 | 5729708 | 0.16592 | 36.7792 | 0.0001 | 35375 | 0.123 | 6417785 | 0.093771 | 72.6476 | 5.787 | 733.62 | 26196 | 537.41 | 4554.41 | 3.76
12 | 17603.89 | 5.53 | 5912388 | 0.18268 | 36.8328 | 0.0536 | 35530 | 0.155 | 6517003 | 0.099218 | 78.2782 | 5.6306 | 733.61 | 26181 | 537.43 | 4558.21 | 3.8
13 | 17609.33 | 5.44 | 6097436 | 0.18505 | 36.8328 | 0 | 35530 | 0 | 6615124 | 0.098121 | 83.7854 | 5.5072 | 733.6 | 26165 | 537.42 | 4561.95 | 3.74
14 | 17615.39 | 6.06 | 6308502 | 0.21107 | 36.8809 | 0.0481 | 35635 | 0.105 | 6727562 | 0.11244 | 90.3619 | 6.5765 | 733.59 | 26149 | 537.41 | 4565.73 | 3.78
15 | 17621.97 | 6.58 | 6497556 | 0.18905 | 36.8809 | 0 | 35737 | 0.102 | 6830206 | 0.10264 | 96.4535 | 6.0916 | 733.58 | 26134 | 537.4 | 4569.27 | 3.54
16 | 17627.42 | 5.45 | 6682898 | 0.18534 | 36.881 | 0.0001 | 35846 | 0.109 | 6919698 | 0.089492 | 101.9527 | 5.4992 | 733.77 | 26432 | 537.59 | 4573.27 | 4
17 | 17632.41 | 4.99 | 6848586 | 0.16569 | 36.9333 | 0.0523 | 35941 | 0.095 | 7009107 | 0.089409 | 107.1342 | 5.1815 | 733.95 | 267.6 | 538.06 | 4576.93 | 3.66
18 | 17637.48 | 5.07 | 6848586 | 0 | 36.9334 | 0.0001 | 35941 | 0 | 7101555 | 0.092448 | 112.6631 | 5.5289 | 733.96 | 26732 | 538.31 | 4580.7 | 3.77
19 | 17643.53 | 6.05 | 7010912 | 0.16233 | 36.9988 | 0.0654 | 36034 | 0.093 | 7192664 | 0.091109 | 118.6242 | 5.9611 | 733.91 | 26653 | 538.29 | 4584.44 | 3.74
20 | 17650.6 | 7.07 | 7126707 | 0.11579 | 37.0592 | 0.0604 | 36134 | 0.1 | 7287073 | 0.094409 | 125.4699 | 6.8457 | 733.87 | 26590 | 538.25 | 4588.24 | 3.8
21 | 17655.6 | 5 | 7288287 | 0.16158 | 37.0904 | 0.0312 | 36228 | 0.094 | 7368647 | 0.081574 | 130.8905 | 5.4206 | 733.84 | 26542 | 538.2 | 4591.94 | 3.7
22 | 17661.56 | 5.96 | 7359944 | 0.071657 | 37.0905 | 0.0001 | 36228 | 0 | 7456313 | 0.087666 | 136.792 | 5.9015 | 733.81 | 26495 | 538.13 | 4595.67 | 3.73
23 | 17667.82 | 6.26 | 7581600 | 0.22166 | 37.1281 | 0.0376 | 36431 | 0.203 | 7550200 | 0.093887 | 142.9849 | 6.1929 | 733.79 | 26464 | 538.1 | 4599.41 | 3.74
24 | 17673.64 | 5.82 | 7734689 | 0.15309 | 37.1282 | 0.0001 | 36555 | 0.124 | 7643438 | 0.093238 | 148.7266 | 5.7417 | 733.76 | 26416 | 538.04 | 4603.23 | 3.82
25 | 17678.65 | 5.01 | 7871287 | 0.1366 | 37.135 | 0.0068 | 36658 | 0.103 | 7735580 | 0.092142 | 154.0747 | 5.3481 | 733.83 | 26527 | 538.36 | 4606.93 | 3.7
26 | 17683.79 | 5.14 | 7871287 | 0 | 37.135 | 0 | 36658 | 0 | 7821810 | 0.08623 | 159.5716 | 5.4969 | 734.04 | 26858 | 539.41 | 4610.66 | 3.73
27 | 17690.47 | 6.68 | 8077952 | 0.20666 | 37.2063 | 0.0713 | 36768 | 0.11 | 7919012 | 0.097202 | 165.6175 | 6.0459 | 734 | 26795 | 539.49 | 4612.63 | 1.97
28 | 17694.89 | 4.42 | 8239928 | 0.16198 | 37.2064 | 0.0001 | 36885 | 0.117 | 8010934 | 0.091922 | 170.7029 | 5.0854 | 733.94 | 26700 | 539.33 | 4612.63 | 0
29 | 17701.24 | 6.35 | 8492268 | 0.25234 | 37.2143 | 0.0079 | 36991 | 0.106 | 8105228 | 0.094294 | 176.9999 | 6.297 | 733.88 | 26605 | 539.15 | 4614.82 | 2.19
30 | 17707.36 | 6.12 | 8693215 | 0.20095 | 37.277 | 0.0627 | 37163 | 0.172 | 8201364 | 0.096136 | 182.6828 | 5.6829 | 733.83 | 26527 | 538.94 | 4618.13 | 3.31
31 | 17712.88 | 5.52 | 9024388 | 0.33117 | 37.3154 | 0.0384 | 37406 | 0.243 | 8298632 | 0.097268 | 188.9261 | 6.2433 | 733.8 | 26479 | 538.73 | 4621.46 | 3.33
Totals | 546443.37 | 177.56 |  | 4.8007 |  | 0.7246 |  | 3.206 |  | 2.9527 |  | 179.9832 |  |  |  |  | 106.57
Average | 17627.2055 | 5.7277 |  | 0.15486 |  | 0.023374 |  | 0.10342 |  | 0.095248 |  | 5.8059 | 733.7906 |  | 538.0719 |  | 3.4377
Min |  | 4.42 |  | 0 |  | 0 |  | 0 |  | 0.081574 |  | 5.0854 | 733.58 |  | 537.4 |  | 0
Max |  | 7.07 |  | 0.33117 |  | 0.0824 |  | 0.312 |  | 0.11244 |  | 6.8457 | 734.04 |  | 539.49 |  | 4
Calculated Values
| Raw Water Added To System (MG) |  |  | 172.7593 |  |  | Raw to Potable Differential |  |  | -1.0652
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 173.8245 |  |  | Average Raw for Month |  |  | 5.7277
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.8701 |  |  | Peak Raw Flow for Month |  |  | 7.07
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | May/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 74 | 0 | 21.1667 | 10.4 | 1.7017 | 0.17083 | 8.55 | 8.64 | 3.8175 | 142 | 151.6667 | 120 | 93 | 5.6667
2 | 68 | 0 | 21 | 9.02 | 1.625 | 0.1565 | 8.58 | 8.7783 | 3.3325 | 150 | 148 | 117 | 87.6667 | 4.3333
3 | 82 | 0 | 21.1667 | 10.3 | 1.9833 | 0.15433 | 8.58 | 8.7283 | 3.4742 | 145 | 142 | 120 | 86.3333 | 4.6667
4 | 81 | 0 | 21.6667 | 10.1 | 2.1383 | 0.1565 | 8.55 | 8.8317 | 3.5983 | 148 | 140.6667 | 117 | 79.6667 | 5.3333
5 | 64 | 0 | 21.3333 | 10.7 | 2.1667 | 0.11067 | 8.6 | 8.7567 | 3.61 | 150 | 147.3333 | 130 | 90 | 4.6667
6 | 64 | 0 | 22.8333 | 15.5 | 2.1533 | 0.1205 | 8.63 | 8.7433 | 3.5833 | 146 | 152.6667 | 115 | 90 | 5
7 | 76 | 0 | 21.8333 | 16.9 | 2.0675 | 0.303 | 8.54 | 8.6667 | 3.4858 | 140 | 139 | 121 | 84 | 5
8 | 71 | 1 | 23 | 10.8 | 1.97 | 0.16267 | 8.53 | 8.98 | 3.6692 | 156 | 132.3333 | 118 | 72.3333 | 6.6667
9 | 65 | 0 | 22.1667 | 11.7 | 2.5783 | 0.18367 | 8.51 | 8.8983 | 3.515 | 143 | 132 | 115 | 79.6667 | 6.3333
10 | 71 | 0 | 21.1667 | 13.5 | 2.6767 | 0.1305 | 8.57 | 8.72 | 3.3582 | 140 | 136.6667 | 110 | 85.6667 | 6
11 | 80 | 0 | 21.5 | 13.9 | 2.8367 | 0.12017 | 8.41 | 8.6617 | 3.8017 | 152 | 143.3333 | 117 | 88.6667 | 4
12 | 64 | 0 | 21.3333 | 14.4 | 2.9017 | 0.097667 | 8.11 | 8.5867 | 3.6992 | 154 | 136.6667 | 120 | 78 | 4.3333
13 | 75 | 0 | 21.8333 | 14 | 2.5983 | 0.10867 | 8.13 | 8.8233 | 3.6425 | 142 | 129.3333 | 115 | 64.3333 | 7.6667
14 | 80 | 0 | 21.6667 | 12.6 | 2.4083 | 0.10417 | 8.31 | 8.8517 | 3.6933 | 145 | 129.3333 | 125 | 64.6667 | 9
15 | 71 | 0 | 22.1667 | 10.6 | 2.5767 | 0.1225 | 8.31 | 8.96 | 3.7683 | 142 | 122.3333 | 113 | 64.6667 | 10
16 | 81 | 0 | 22.1667 | 12.4 | 2.604 | 0.093333 | 8.39 | 8.7833 | 3.5225 | 143 | 135 | 114 | 79.6667 | 6.6667
17 | 68 | 0 | 21.5 | 13 | 2.4767 | 0.10333 | 8.3 | 8.9017 | 3.6458 | 140 | 129.3333 | 114 | 68.6667 | 7.6667
18 | 76 | 0 | 21.6667 | 12.9 | 2.25 | 0.104 | 8.5 | 8.9217 | 3.4908 | 141 | 126.3333 | 113 | 69 | 4.6667
19 | 68 | 0 | 21.8333 | 8.65 | 2.3683 | 0.093333 | 8.47 | 8.8133 | 3.7483 | 140 | 137.6667 | 125 | 79.3333 | 4
20 | 72 | 0 | 22.1667 | 9.86 | 2.4833 | 0.11333 | 8.36 | 8.885 | 3.8183 | 137 | 140.3333 | 111 | 81.6667 | 7.6667
21 | 72 | 0 | 22.3333 | 9.86 | 2.134 | 0.13967 | 8.24 | 8.8183 | 3.5592 | 137 | 144.6667 | 111 | 81 | 5.6667
22 | 89 | 0 | 21.8333 | 8.39 | 2.3033 | 0.138 | 8.39 | 8.9017 | 3.4258 | 140 | 136.3333 | 112 | 84.3333 | 7.6667
23 | 68 | 0 | 23 | 10.5 | 2.37 | 0.11883 | 8.29 | 8.895 | 3.5358 | 142 | 130.3333 | 118 | 73.3333 | 5
24 | 74 | 0.1 | 22.8333 | 8.94 | 2.0267 | 0.12467 | 8.34 | 8.8467 | 3.5517 | 138 | 142 | 118 | 76.6667 | 6.6667
25 | 64 | 2.2 | 22.6667 | 9.58 | 1.8617 | 0.095167 | 8.32 | 8.8733 | 3.435 | 145 | 134 | 114 | 77.6667 | 3.6667
26 | 64 | 0 | 22.6667 | 9.99 | 1.874 | 0.11133 | 8.49 | 8.9533 | 3.4242 | 132 | 127.6667 | 110 | 71.3333 | 5.6667
27 | 66 | 0 | 23 | 10 | 2.66 | 0.13083 | 8.57 | 8.9633 | 3.8317 | 149 | 103.6667 | 109 | 78 | 6
28 | 75 | 0 | 22.3333 | 8.74 | 2.366 | 0.14283 | 8.47 | 8.9583 | 3.5342 | 134 | 138.6667 | 110 | 76.6667 | 6.3333
29 | 64 | 0 | 23.1667 | 4.5 | 2.0283 | 0.161 | 8.67 | 8.8033 | 3.4917 | 135 | 130.3333 | 108 | 78 | 6
30 | 80 | 0 | 23.3333 | 6.7 | 2.535 | 0.1335 | 8.57 | 8.7217 | 3.6667 | 135 | 134.6667 | 104 | 78.3333 | 8
31 | 72 | 0 | 23.1667 | 6.71 | 2.1333 | 0.13967 | 8.34 | 8.905 | 3.6958 | 131 | 119.3333 | 106 | 61.6667 | 6
TOTAL |  | 3.3
AVG. | 72.2258 | 0.10645 | 22.1129 | 10.811 | 2.2857 | 0.13372 | 8.4394 | 8.8249 | 3.5944 | 142.3871 | 135.2796 | 115.1613 | 78.1935 | 6
MAX. | 89 | 2.2 | 23.3333 | 16.9 | 2.9017 | 0.303 | 8.67 | 8.98 | 3.8317 | 156 | 152.6667 | 130 | 93 | 10
MIN. | 64 | 0 | 21 | 4.5 | 1.625 | 0.093333 | 8.11 | 8.5867 | 3.3325 | 131 | 103.6667 | 104 | 61.6667 | 3.6667

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: May 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 4 | 24 | 88 | 0.96 | 90 | 1 | 53 | 2273.92 | 560 | 495.9 | 60 | 43.3469 | 9.4532 | 1.0103 | 10.6751 | 1.1438
2 | 3 | 24 | 104 | 2.73 | 312 | 3 | 47 | 2060.74 | 280 | 427.5 | 52 | 41.3888 | 8.5861 | 0.94397 | 5.6236 | 1.0444
3 | 4 | 24 | 0 | 0 | 0 | 0 | 42 | 1879.86 | 320 | 384.75 | 27 | 42.4488 | 8.688 | 0.94839 | 7.2259 | 0.60968
4 | 4 | 24 | 0 | 0 | 0 | 0 | 50 | 2112.42 | 260 | 427.5 | 44 | 42.2851 | 8.5574 | 1.0009 | 5.2045 | 0.88076
5 | 4 | 24 | 0 | 0 | 0 | 0 | 53 | 2138.26 | 380 | 453.15 | 40 | 41.7567 | 8.8493 | 1.035 | 7.4208 | 0.78113
6 | 4 | 24 | 115 | 4.45 | 102 | 1 | 54 | 2067.2 | 260 | 453.15 | 8 | 42.154 | 9.2406 | 1.1012 | 5.3019 | 0.16313
7 | 4 | 24 | 101 | 0.51 | 128 | 1 | 58 | 2157.64 | 320 | 470.25 | 30 | 41.8624 | 9.1238 | 1.1253 | 6.2086 | 0.58206
8 | 4 | 24 | 98 | 1 | 137 | 1 | 46 | 1737.74 | 320 | 384.75 | 21 | 42.1786 | 9.3387 | 1.1165 | 7.7671 | 0.50971
9 | 3 | 24 | 0 | 0 | 0 | 0 | 43 | 1750.66 | 160 | 384.75 | 11 | 42.3208 | 9.301 | 1.0395 | 3.8679 | 0.26592
10 | 4 | 24 | 93 | 0.48 | 133 | 1 | 46 | 1841.1 | 380 | 410.4 | 33 | 42.8651 | 9.5551 | 1.071 | 8.8473 | 0.76832
11 | 5 | 24 | 100 | 0.68 | 121 | 1 | 53 | 2170.56 | 360 | 513 | 57 | 41.7751 | 9.8733 | 1.0201 | 6.9286 | 1.097
12 | 3 | 24 | 94 | 4.9 | 157 | 1 | 44 | 2073.66 | 270 | 470.25 | 67 | 44.9621 | 10.1962 | 0.95403 | 5.8543 | 1.4527
13 | 4 | 24 | 0 | 0 | 0 | 0 | 44 | 2099.5 | 290 | 470.25 | 28 | 46.2755 | 10.3649 | 0.96981 | 6.3919 | 0.61715
14 | 6 | 24 | 97 | 0.51 | 105 | 1 | 48 | 2241.62 | 360 | 538.65 | 31 | 44.353 | 10.6578 | 0.94974 | 7.123 | 0.61337
15 | 5 | 23 | 96 | 0.03 | 102 | 1 | 54 | 2080.12 | 310 | 495.9 | 35 | 37.905 | 9.0365 | 0.98402 | 5.649 | 0.63779
16 | 5 | 21 | 116 | 0.96 | 109 | 1 | 45 | 2002.6 | 420 | 453.15 | 32 | 44.0587 | 9.9696 | 0.99003 | 9.2403 | 0.70402
17 | 3 | 24 | 90 | 0.48 | 95 | 1 | 44 | 2228.7 | 210 | 470.25 | 42 | 53.5531 | 11.2996 | 1.0573 | 5.0461 | 1.0092
18 | 3 | 24 | 0 | 0 | 0 | 0 | 44 | 1821.72 | 240 | 410.4 | 33 | 43.0832 | 9.7058 | 1.0406 | 5.6759 | 0.78044
19 | 4 | 24 | 114 | 0.67 | 93 | 1 | 53 | 2144.72 | 240 | 538.65 | 59 | 42.5059 | 10.6754 | 1.0504 | 4.7565 | 1.1693
20 | 4 | 24 | 124 | 0.68 | 100 | 1 | 57 | 2428.96 | 400 | 555.75 | 18 | 41.1941 | 9.4253 | 0.96669 | 6.7838 | 0.30527
21 | 4 | 17 | 117 | 0.48 | 74 | 1 | 36 | 1737.74 | 260 | 367.65 | 29 | 41.6724 | 8.8165 | 0.86331 | 6.235 | 0.69544
22 | 4 | 24 | 0 | 0 | 0 | 0 | 54 | 2105.96 | 320 | 470.25 | 53 | 42.368 | 9.4606 | 1.0864 | 6.4378 | 1.0663
23 | 4 | 24 | 95 | 2 | 203 | 2 | 51 | 2183.48 | 300 | 538.65 | 56 | 41.8224 | 10.3173 | 0.97685 | 5.7462 | 1.0726
24 | 5 | 24 | 90 | 2.2 | 124 | 1 | 48 | 2125.34 | 340 | 453.15 | 39 | 43.7864 | 9.3358 | 0.9889 | 7.0047 | 0.80348
25 | 4 | 24 | 112 | 0.96 | 103 | 1 | 44 | 1892.78 | 80 | 384.75 | 38 | 45.2998 | 9.2082 | 1.053 | 1.9146 | 0.90945
26 | 5 | 21.25 | 0 | 0 | 0 | 0 | 53 | 1931.54 | 280 | 410.4 | 56 | 45.0583 | 9.5737 | 1.2364 | 6.5317 | 1.3063
27 | 5 | 24 | 94 | 0.5 | 110 | 1 | 54 | 2422.5 | 350 | 470.25 | 66 | 43.4832 | 8.4409 | 0.96928 | 6.2824 | 1.1847
28 | 5 | 18 | 90 | 0.73 | 117 | 1 | 36 | 1576.24 | 410 | 324.9 | 31 | 42.7596 | 8.8138 | 0.97659 | 11.1223 | 0.84096
29 | 5 | 24 | 95 | 0.51 | 106 | 1 | 54 | 2293.3 | 160 | 555.75 | 44 | 43.3033 | 10.494 | 1.0197 | 3.0212 | 0.83083
30 | 6 | 24 | 106 | 1.23 | 152 | 2 | 53 | 2170.56 | 240 | 495.9 | 50 | 42.526 | 9.7158 | 1.0384 | 4.7021 | 0.97961
31 | 4 | 24 | 107 | 0.96 | 127 | 1 | 48 | 1957.38 | 260 | 453.15 | 25 | 42.5177 | 9.8432 | 1.0426 | 5.6477 | 0.54304
TOTAL |  | 724.25 |  |  | 2900 | 27 | 1509 | 63708.52 | 9340 | 14133.15 | 1190
AVG | 4.2258 |  | 75.3548 | 0.9229 | 93.5484 | 0.87097 | 48.6774 | 2017.2818 | 301.2903 | 436.8273 | 39.6667 | 43.5873 | 9.5457 | 1.0202 | 6.3303 | 0.81832
MIN | 3 |  | 0 | 0 | 0 | 0 | 36 | 1737.74 | 80 | 384.75 | 8 | 37.905 | 8.4409 | 0.86331 | 1.9146 | 0.16313
MAX | 6 |  | 124 | 4.9 | 312 | 3 | 58 | 2273.92 | 560 | 513 | 67 | 53.5531 | 11.2996 | 1.2364 | 11.1223 | 1.4527

## Monthly Chemical Report
Month, Year: |  | May/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #NAME?
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 6.29 | 542.19 | 9.2233 | 58.0143 | 4547.84 | 68.3261 | 429.7709 | 560 | 32.0064 | 201.32 | 495.9 | 57.5528 | 362.007 | [9 empty] | 60 | 19.9793 | 125.67 | 207.57 | 187.0878 | 1384.3522
2 | 5.97 | 480.81 | 8.6175 | 51.4467 | 4121.48 | 65.2395 | 389.4799 | 280 | 16.861 | 100.66 | 427.5 | 52.2739 | 312.075 | [9 empty] | 52 | 18.2436 | 108.914 | 197.01 | 161.2354 | 1159.5855
3 | 5.31 | 429.66 | 8.6579 | 45.9736 | 3759.72 | 66.9103 | 355.2935 | 320 | 21.6648 | 115.04 | 384.75 | 52.8941 | 280.8675 | [9 empty] | 27 | 10.65 | 56.5515 | 175.23 | 160.7771 | 1028.9562
4 | 5.99 | 511.5 | 9.137 | 54.7305 | 4224.84 | 66.6523 | 399.2474 | 260 | 15.6043 | 93.47 | 427.5 | 52.0993 | 312.075 | [9 empty] | 44 | 15.3853 | 92.158 | 197.67 | 158.8783 | 1149.3509
5 | 6.14 | 542.19 | 9.4486 | 58.0143 | 4276.52 | 65.8194 | 404.1311 | 380 | 22.2492 | 136.61 | 453.15 | 53.8761 | 330.7995 | [9 empty] | 40 | 13.645 | 83.78 | 202.62 | 165.0383 | 1215.955
6 | 5.88 | 552.42 | 10.0525 | 59.1089 | 4134.4 | 66.4457 | 390.7008 | 260 | 15.8963 | 93.47 | 453.15 | 56.2584 | 330.7995 | [9 empty] | 8 | 2.8497 | 16.756 | 194.04 | 151.5026 | 1084.8752
7 | 6.18 | 593.34 | 10.273 | 63.4874 | 4315.28 | 65.9861 | 407.794 | 320 | 18.6149 | 115.04 | 470.25 | 55.5473 | 343.2825 | [9 empty] | 30 | 10.1675 | 62.835 | 203.94 | 160.5888 | 1196.3788
8 | 4.94 | 470.58 | 10.1927 | 50.3521 | 3475.48 | 66.4844 | 328.4329 | 320 | 23.2874 | 115.04 | 384.75 | 56.8558 | 280.8675 | [9 empty] | 21 | 8.9037 | 43.9845 | 163.02 | 165.7241 | 981.6969
9 | 4.96 | 439.89 | 9.4896 | 47.0682 | 3501.32 | 66.7086 | 330.8747 | 160 | 11.5968 | 57.52 | 384.75 | 56.6265 | 280.8675 | [9 empty] | 11 | 4.6451 | 23.0395 | 163.68 | 149.0665 | 903.05
10 | 5.15 | 470.58 | 9.7771 | 50.3521 | 3682.2 | 67.5666 | 347.9679 | 380 | 26.5262 | 136.61 | 410.4 | 58.1732 | 299.592 | [9 empty] | 33 | 13.4211 | 69.1185 | 169.95 | 175.4642 | 1073.5905
11 | 6.23 | 542.19 | 9.3121 | 58.0143 | 4341.12 | 65.8484 | 410.2358 | 360 | 20.7737 | 129.42 | 513 | 60.1108 | 374.49 | [9 empty] | 57 | 19.1632 | 119.3865 | 205.59 | 175.2081 | 1297.1367
12 | 5.53 | 450.12 | 8.7094 | 48.1628 | 4147.32 | 70.8719 | 391.9217 | 270 | 17.5524 | 97.065 | 470.25 | 62.0764 | 343.2825 | [9 empty] | 67 | 25.3764 | 140.3315 | 182.49 | 184.5865 | 1203.2536
13 | 5.44 | 450.12 | 8.8535 | 48.1628 | 4199 | 72.9422 | 396.8055 | 290 | 19.1645 | 104.255 | 470.25 | 63.1034 | 343.2825 | [9 empty] | 28 | 10.7805 | 58.646 | 179.52 | 174.8441 | 1130.6718
14 | 6.06 | 491.04 | 8.6702 | 52.5413 | 4483.24 | 69.9119 | 423.6662 | 360 | 21.3564 | 129.42 | 538.65 | 64.8869 | 393.2145 | [9 empty] | 31 | 10.7144 | 64.9295 | 199.98 | 175.5398 | 1263.7515
15 | 6.58 | 552.42 | 8.9831 | 59.1089 | 4160.24 | 59.7481 | 393.1427 | 310 | 16.9369 | 111.445 | 495.9 | 55.0163 | 362.007 | [9 empty] | 35 | 11.141 | 73.3075 | 217.14 | 151.8254 | 1216.1511
16 | 5.45 | 460.35 | 9.0381 | 49.2574 | 4005.2 | 69.448 | 378.4914 | 420 | 27.7046 | 150.99 | 453.15 | 60.6972 | 330.7995 | [9 empty] | 32 | 12.298 | 67.024 | 179.85 | 179.1858 | 1156.4123
17 | 4.99 | 450.12 | 9.6519 | 48.1628 | 4457.4 | 84.4137 | 421.2243 | 210 | 15.1293 | 75.495 | 470.25 | 68.7941 | 343.2825 | [9 empty] | 42 | 17.6291 | 87.969 | 164.67 | 195.618 | 1140.8036
18 | 5.07 | 450.12 | 9.4996 | 48.1628 | 3643.44 | 67.9103 | 344.3051 | 240 | 17.0178 | 86.28 | 410.4 | 59.0911 | 299.592 | [9 empty] | 33 | 13.6328 | 69.1185 | 167.31 | 167.1516 | 1014.7684
19 | 6.05 | 542.19 | 9.5891 | 58.0143 | 4289.44 | 67.0003 | 405.3521 | 240 | 14.2612 | 86.28 | 538.65 | 64.9941 | 393.2145 | [9 empty] | 59 | 20.4257 | 123.5755 | 199.65 | 176.2705 | 1266.0864
20 | 7.07 | 583.11 | 8.825 | 62.3928 | 4857.92 | 64.9326 | 459.0734 | 400 | 20.3395 | 143.8 | 555.75 | 57.383 | 405.6975 | [9 empty] | 18 | 5.3325 | 37.701 | 233.31 | 156.8125 | 1341.9747
21 | 5 | 368.28 | 7.8812 | 39.406 | 3475.48 | 65.6866 | 328.4329 | 260 | 18.694 | 93.47 | 367.65 | 53.6769 | 268.3845 | [9 empty] | 29 | 12.1481 | 60.7405 | 165 | 158.0868 | 955.4338
22 | 5.96 | 552.42 | 9.9176 | 59.1089 | 4211.92 | 66.783 | 398.0264 | 320 | 19.302 | 115.04 | 470.25 | 57.5977 | 343.2825 | [9 empty] | 53 | 18.6256 | 111.0085 | 196.68 | 172.2259 | 1223.1464
23 | 6.26 | 521.73 | 8.9177 | 55.8251 | 4366.96 | 65.923 | 412.6777 | 300 | 17.2284 | 107.85 | 538.65 | 62.8138 | 393.2145 | [9 empty] | 56 | 18.7367 | 117.292 | 206.58 | 173.6197 | 1293.4393
24 | 5.82 | 491.04 | 9.0277 | 52.5413 | 4250.68 | 69.0188 | 401.6893 | 340 | 21.0017 | 122.23 | 453.15 | 56.8384 | 330.7995 | [9 empty] | 39 | 14.0353 | 81.6855 | 192.06 | 169.9219 | 1181.0055
25 | 5.01 | 450.12 | 9.6133 | 48.1628 | 3785.56 | 71.4043 | 357.7354 | 80 | 5.7405 | 28.76 | 384.75 | 56.0614 | 280.8675 | [9 empty] | 38 | 15.8864 | 79.591 | 165.33 | 158.7059 | 960.4468
26 | 5.14 | 542.19 | 11.2868 | 58.0143 | 3863.08 | 71.0236 | 365.0611 | 280 | 19.5837 | 100.66 | 410.4 | 58.2864 | 299.592 | [9 empty] | 56 | 22.8195 | 117.292 | 169.62 | 182.9999 | 1110.2394
27 | 6.68 | 552.42 | 8.8486 | 59.1089 | 4845 | 68.5408 | 457.8525 | 350 | 18.8361 | 125.825 | 470.25 | 51.3896 | 343.2825 | [9 empty] | 66 | 20.6942 | 138.237 | 220.44 | 168.3093 | 1344.7459
28 | 4.42 | 368.28 | 8.9154 | 39.406 | 3152.48 | 67.4003 | 297.9094 | 410 | 33.3473 | 147.395 | 324.9 | 53.66 | 237.177 | [9 empty] | 31 | 14.6899 | 64.9295 | 145.86 | 178.0129 | 932.6768
29 | 6.35 | 552.42 | 9.3085 | 59.1089 | 4586.6 | 68.2573 | 433.4337 | 160 | 9.0583 | 57.52 | 555.75 | 63.8894 | 405.6975 | [9 empty] | 44 | 14.5131 | 92.158 | 209.55 | 165.0265 | 1257.4681
30 | 6.12 | 542.19 | 9.4795 | 58.0143 | 4341.12 | 67.032 | 410.2358 | 240 | 14.098 | 86.28 | 495.9 | 59.1515 | 362.007 | [9 empty] | 50 | 17.1119 | 104.725 | 201.96 | 166.8729 | 1223.2222
31 | 5.52 | 491.04 | 9.5183 | 52.5413 | 3914.76 | 67.019 | 369.9448 | 260 | 16.933 | 93.47 | 453.15 | 59.9274 | 330.7995 | [9 empty] | 25 | 9.486 | 52.3625 | 182.16 | 162.8837 | 1081.2781
Total | 177.56 |  |  | 1651.7665 |  |  | 12040.9103 |  |  | 3357.73 |  |  | 10317.1995 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 2544.8175 | 5859.48 | 5229.0706 | 35771.9038
Avg. | 5.7277 | 497.97 | 9.3134 | 53.2828 | 4110.2271 | 67.976 | 388.4165 | 301.2903 | 18.9796 | 108.3139 | 455.9081 | 58.1162 | 332.8129 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 39.1935 | 14.2945 | 82.0909 | 189.0155 | 201.4638 | 1153.9324
Max | 7.07 | 593.34 | 11.2868 | 63.4874 | 4857.92 | 84.4137 | 459.0734 | 560 | 33.3473 | 201.32 | 555.75 | 68.7941 | 405.6975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 25.3764 | 140.3315 | 233.31 | 195.618 | 1384.3522
Min. | 4.42 | 368.28 | 7.8812 | 39.406 | 3152.48 | 59.7481 | 297.9094 | 80 | 5.7405 | 28.76 | 324.9 | 51.3896 | 237.177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2.8497 | 16.756 | 145.86 | 149.0665 | 903.05
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 2.0945 | Lime | 33 | Per MGD
|  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract |  | 0.20146 | PerKG

## LAS Meter
Month:
LAS Carrier Water Meter
Prev. | 482760
1 | 523570 | 40810
2 | 563290 | 39720
3 | 603790 | 40500
4 | 644450 | 40660
5 | 685690 | 41240
6 | 725050 | 39360
7 | 766670 | 41620
8 | 807280 | 40610
9 | 847290 | 40010
10 | 887470 | 40180
11 | 927440 | 39970
12 | 968360 | 40920
13 | 1008420 | 40060
14 | 1049160 | 40740
15 | 1087540 | 38380
16 | 1129800 | 42260
17 | 1170040 | 40240
18 | 1210390 | 40350
19 | 1250340 | 39950
20 | 1291510 | 41170
21 | 1324200 | 32690
22 | 1361030 | 36830
23 | 1401450 | 40420
24 | 1443010 | 41560
25 | 1482950 | 39940
26 | 1518430 | 35480
27 | 1560080 | 41650
28 | 1599190 | 39110
29 | 1639540 | 40350
30 | 1679950 | 40410
31 | 1720210 | 40260
Total |  | 1237450

## Graphs
Chemicals | Amount
LAS | 0
Fe | 12040.9103
CL2 | 3357.73
Poly | 10317.1995
Potassium | 2544.8175
Lime | 0
Chemfloc 3315 | 35771.9038