## Pumpage
Water Treatment Plant Pumpage Report - MG
All Readings Taken @ 12:01 AM on Date Indicated
Month, Year: October 2020
Date | Raw Water Meter | Raw Water Treated | Reclaim Meter | Reclaim Pumpage | Centrate Meter | Centrate Pumpage | Backwash Meter | Backwash Pumpage | Potable Meter | Potable Flow | H.S. Meter | H.S. Pumpage | Cleburne Lake Level (ft) | Reservoir Storage (acre-ft) | Aquila Lake Level (ft) | Aquila Meter | Aquila Flow MGD | Golf Course Meter | Golf Course Flow MG
0 | 18619.6 |  | 9665254 |  | 40.983 |  | 51268 |  | 4589172 |  | 1111.927 |  |  |  |  | 5028.57
1 | 18625.08 | 5.48 | 9665254 | 0 | 40.9994 | 0.0164 | 51268 | 0 | 4717788 | 0.12862 | 1117.984 | 6.057 | 732.14 | 23908 | 537.03 | 5031.89 | 3.32
2 | 18632.85 | 7.77 | 9936824 | 0.27157 | 41.0575 | 0.0581 | 51558 | 0.29 | 4851056 | 0.13327 | 1125.686 | 7.702 | 732.11 | 23862 | 537 | 5035.33 | 3.44
3 | 18638.62 | 5.77 | 10277296.3 | 0.34047 | 41.0578 | 0.0003 | 51684 | 0.126 | 4976500 | 0.12544 | 1131.749 | 6.063 | 732.08 | 23816 | 536.96 | 5038.72 | 3.39
4 | 18645.8 | 7.18 | 10277296.3 | 0 | 41.0861 | 0.0283 | 51684 | 0 | 5108888 | 0.13239 | 1138.706 | 6.957 | 732.07 | 23801 | 536.95 | 5042.13 | 3.41
5 | 18652.5 | 6.7 | 10277297.4 | 1.1e-06 | 41.0866 | 0.0005 | 51793 | 0.109 | 5240200 | 0.13131 | 1145.805 | 7.099 | 732.04 | 23755 | 536.92 | 5045.52 | 3.39
6 | 18659.59 | 7.09 | 10397849 | 0.12055 | 41.0869 | 0.0003 | 51883 | 0.09 | 5373650 | 0.13345 | 1152.98 | 7.175 | 732.02 | 23725 | 536.9 | 5048.9 | 3.38
7 | 18666.76 | 7.17 | 10683879.6 | 0.28603 | 41.1145 | 0.0276 | 52018 | 0.135 | 5507985 | 0.13434 | 1160.416 | 7.436 | 732.01 | 23710 | 536.89 | 5052.34 | 3.44
8 | 18673.56 | 6.8 | 10683879.6 | 0 | 41.1601 | 0.0456 | 52018 | 0 | 5639623 | 0.13164 | 1167.134 | 6.718 | 731.99 | 23679 | 536.88 | 5055.74 | 3.4
9 | 18681.52 | 7.96 | 10831501.8 | 0.14762 | 41.1663 | 0.0062 | 52136 | 0.118 | 5772680 | 0.13306 | 1174.419 | 7.285 | 731.98 | 23664 | 536.86 | 5059.17 | 3.43
10 | 18687.72 | 6.2 | 11012672 | 0.18117 | 41.2012 | 0.0349 | 52294 | 0.158 | 5906638 | 0.13396 | 1181.733 | 7.314 | 731.92 | 23661 | 536.79 | 5062.55 | 3.38
11 | 18694.47 | 6.75 | 11169723 | 0.15705 | 41.2229 | 0.0217 | 52294 | 0 | 6039522 | 0.13288 | 1188.726 | 6.993 | 731.94 | 23603 | 536.82 | 5065.94 | 3.39
12 | 18701.9 | 7.43 | 11169723 | 0 | 41.2236 | 0.0007 | 52471 | 0.177 | 6174200 | 0.13468 | 1196.206 | 7.48 | 731.93 | 23588 | 536.82 | 5069.33 | 3.39
13 | 18708.56 | 6.66 | 11317830 | 0.14811 | 41.2245 | 0.0009 | 52569 | 0.098 | 6310957 | 0.13676 | 1203.486 | 7.28 | 731.89 | 23527 | 536.78 | 5072.77 | 3.44
14 | 18716.13 | 7.57 | 11439797 | 0.12197 | 41.2254 | 0.0009 | 52569 | 0 | 6444100 | 0.13314 | 1210.677 | 7.191 | 731.87 | 23497 | 536.75 | 5076.15 | 3.38
15 | 18722.26 | 6.13 | 11532771 | 0.092974 | 41.2894 | 0.064 | 52682 | 0.113 | 6579727 | 0.13563 | 1217.359 | 6.682 | 731.86 | 23482 | 536.75 | 5079.61 | 3.46
16 | 18728.64 | 6.38 | 11678296 | 0.14552 | 41.2904 | 0.001 | 52682 | 0 | 6708740 | 0.12901 | 1223.634 | 6.275 | 731.82 | 23421 | 536.72 | 5082.91 | 3.3
17 | 18734.73 | 6.09 | 11903963 | 0.22567 | 41.3372 | 0.0468 | 52880 | 0.198 | 6842530 | 0.13379 | 1230.18 | 6.546 | 731.78 | 23345 | 536.63 | 5086.4 | 3.49
18 | 18740.8 | 6.07 | 12060747 | 0.15678 | 41.3444 | 0.0072 | 52927 | 0.047 | 6979700 | 0.13717 | 1236.601 | 6.421 | 731.77 | 23345 | 536.63 | 5089.81 | 3.41
19 | 18748.64 | 7.84 | 12076971 | 0.016224 | 41.3455 | 0.0011 | 53172 | 0.245 | 7119850 | 0.14015 | 1244.083 | 7.482 | 731.67 | 23194 | 536.65 | 5093.24 | 3.43
20 | 18755.41 | 6.77 | 12223652 | 0.14668 | 41.3466 | 0.0011 | 53172 | 0 | 7255500 | 0.13565 | 1250.962 | 6.879 | 731.64 | 23149 | 536.62 | 5096.64 | 3.4
21 | 18761.7 | 6.29 | 12346228 | 0.12258 | 41.4009 | 0.0543 | 53172 | 0 | 7395700 | 0.1402 | 1257.475 | 6.513 | 731.63 | 23134 | 536.61 | 5100.06 | 3.42
22 | 18768.29 | 6.59 | 12346228 | 0 | 41.4329 | 0.032 | 53267 | 0.095 | 7540320 | 0.14462 | 1264.024 | 6.549 | 731.62 | 23119 | 536.59 | 5103.51 | 3.45
23 | 18773.85 | 5.56 | 12346228 | 0 | 41.4341 | 0.0012 | 53267 | 0 | 7691150 | 0.15083 | 1269.99 | 5.966 | 731.63 | 23134 | 536.62 | 5106.95 | 3.44
24 | 18778.82 | 4.97 | 12503019 | 0.15679 | 41.478 | 0.0439 | 53267 | 0 | 7846100 | 0.15495 | 1275.009 | 5.019 | 731.63 | 23134 | 536.6 | 5110.38 | 3.43
25 | 18784.37 | 5.55 | 12751906 | 0.24889 | 41.503 | 0.025 | 53468 | 0.201 | 7991100 | 0.145 | 1280.702 | 5.693 | 731.61 | 23104 | 536.58 | 5113.76 | 3.38
26 | 18789.53 | 5.16 | 12982804 | 0.2309 | 41.5042 | 0.0012 | 53689 | 0.221 | 8140350 | 0.14925 | 1286.034 | 5.332 | 731.63 | 23134 | 536.59 | 5117.21 | 3.45
27 | 18794.59 | 5.06 | 13181986 | 0.19918 | 41.5053 | 0.0011 | 53807 | 0.118 | 8289578 | 0.14923 | 1291.343 | 5.309 | 731.6 | 23088 | 536.58 | 5120.69 | 3.48
28 | 18799.86 | 5.27 | 13296453 | 0.11447 | 41.5482 | 0.0429 | 53926 | 0.119 | 8431610 | 0.14203 | 1296.802 | 5.459 | 731.6 | 23088 | 536.58 | 5124.1 | 3.41
29 | 18806.06 | 6.2 | 13452060 | 0.15561 | 41.549 | 0.0008 | 53926 | 0 | 8575770 | 0.14416 | 1303.392 | 6.59 | 731.59 | 23073 | 536.57 | 5127.58 | 3.48
30 | 18812.45 | 6.39 | 13542112 | 0.090052 | 41.5846 | 0.0356 | 54026 | 0.1 | 8723875 | 0.1481 | 1309.576 | 6.184 | 731.58 | 23058 | 536.55 | 5131.02 | 3.44
31 | 18817.92 | 5.47 | 13638925 | 0.096813 | 41.5973 | 0.0127 | 54108 | 0.082 | 8868700 | 0.14483 | 1315.149 | 5.573 | 731.56 | 23028 | 536.53 | 5134.42 | 3.4
Totals | 580502.98 | 198.32 |  | 3.9737 |  | 0.6143 |  | 2.84 |  | 4.2795 |  | 203.222 |  |  |  |  | 105.85
Average | 18725.9026 | 6.3974 |  | 0.12818 |  | 0.019816 |  | 0.091613 |  | 0.13805 |  | 6.5555 | 731.8132 |  | 536.7339 |  | 3.4145
Min |  | 4.97 |  | 0 |  | 0.0003 |  | 0 |  | 0.12544 |  | 5.019 | 731.56 |  | 536.53 |  | 3.3
Max |  | 7.96 |  | 0.34047 |  | 0.064 |  | 0.29 |  | 0.15495 |  | 7.702 | 732.14 |  | 537.03 |  | 3.49
Calculated Values
| Raw Water Added To System (MG) |  |  | 194.3463 |  |  | Raw to Potable Differential |  |  | -1.7561
(Raw pumpage minus reclaim pumpage)
| Potable Water to Distribution (MG) |  |  | 196.1025 |  |  | Average Raw for Month |  |  | 6.3974
(High service minus plant potable minus Backwash)
| Reclaim Checksum |  |  | 0.51937 |  |  | Peak Raw Flow for Month |  |  | 7.96
(Reclaim minus centrate minus backwash)
Remainder should tie to known water usage
such as re-wash or floc basin draining.

## Water Quality
WATER TREATMENT PLANT MONTHLY WATER QUALITY REPORT | [10 empty] | Month, Year: |  | October/1/2020
Date | AIR TEMP F° (Min) | RAINFALL (IN.) | WATER TEMP. C° | ANALYTICAL RESULTS
|  |  |  | TURBIDITY |  |  | pH |  | RES. Cl2 | TOTAL HARD "V" |  | TOTAL ALKALINITY |  | P ALKALINITY
|  |  |  | RAW | SETTLED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP) | RAW | FINISHED (TAP) | RAW | FINISHED (TAP) | FINISHED (TAP)
1 | 60 | 0 | 21.8333 | 9.69 | 3.248 | 0.10733 | 8.81 | 8.955 | 3.7883 | 112 | 127.6667 | 76 | 64.3333 | 6
2 | 61 | 0 | 22.6667 | 11.5 | 2.6683 | 0.098 | 8.99 | 8.8167 | 4.0317 | 116 | 127 | 82 | 64.3333 | 3
3 | 68 | 0 | 22 | 11.1 | 2.1583 | 0.112 | 8.61 | 8.8817 | 4.0767 | 115 | 127.6667 | 85 | 58.3333 | 3.6667
4 | 61 | 0 | 21.8333 | 7.98 | 2.765 | 0.098667 | 8.86 | 8.9067 | 3.955 | 120 | 127.3333 | 88 | 60.6667 | 3
5 | 69 | 0 | 21 | 12.5 | 2.3183 | 0.067 | 8.822 | 8.5017 | 3.9367 | 112 | 144.6667 | 85 | 68 | 2
6 | 71 | 0 | 21.6667 | 9.49 | 2.48 | 0.0725 | 8.51 | 8.6467 | 3.52 | 115 | 130.6667 | 81 | 69.6667 | 3
7 | 61 | 0 | 22.1667 | 8.2 | 2.2183 | 0.075167 | 8.83 | 8.495 | 4.0642 | 120 | 133.6667 | 76 | 65 | 3.3333
8 | 72 | 0 | 22 | 6.8 | 2.6933 | 0.085 | 8.81 | 8.7267 | 3.5917 | 103 | 131 | 82 | 69.3333 | 1.6667
9 | 63 | 0 | 22.6667 | 10.2 | 2.8483 | 0.082667 | 8.91 | 8.67 | 3.9775 | 108 | 125.3333 | 76 | 65.3333 | 2.6667
10 | 74 | 0 | 22 | 7.12 | 2.1233 | 0.088333 | 9.12 | 8.65 | 3.6492 | 100 | 120 | 68 | 63 | 2.3333
11 | 79 | 0 | 21.6667 | 7.67 | 2.505 | 0.071 | 8.85 | 8.5567 | 3.7467 | 118 | 135.3333 | 73 | 70 | 1.6667
12 | 58 | 0 | 21.8333 | 9.05 | 2.5633 | 0.066 | 8.78 | 8.3867 | 4.1175 | 133 | 130 | 78 | 68.3333 | 1
13 | 55 | 0 | 22.8333 | 10.1 | 2.3967 | 0.072833 | 8.42 | 8.405 | 3.4433 | 112 | 127.3333 | 80 | 65.3333 | 1.6667
14 | 78 | 0 | 21.5 | 9.4 | 2.6367 | 0.08 | 8.46 | 8.5233 | 3.8408 | 105 | 145.3333 | 78 | 67.6667 | 0
15 | 58 | 0 | 22.1667 | 9.74 | 2.6767 | 0.0745 | 8.46 | 8.75 | 3.94 | 100 | 135 | 75 | 76.3333 | 5.6667
16 | 55 | 0 | 22 | 10.4 | 2.5833 | 0.080667 | 8.48 | 8.5133 | 3.2767 | 140 | 136.6667 | 77 | 72 | 1
17 | 73 | 0 | 21.5 | 9.83 | 2.6733 | 0.099833 | 8.74 | 8.7133 | 4.2383 | 109 | 130 | 77 | 71.3333 | 3
18 | 61 | 0 | 21.3333 | 11.7 | 2.5133 | 0.10267 | 8.28 | 8.31 | 3.8458 | 120 | 132 | 81 | 66 | 1.3333
19 | 61 | 0 | 20.8333 | 8.73 | 2.5767 | 0.10133 | 8.43 | 8.5117 | 4.5983 | 110 | 133.6667 | 80 | 55.6667 | 1.3333
20 | 75 | 0 | 21.1667 | 16.9 | 2.7783 | 0.079 | 8.33 | 8.66 | 3.555 | 138 | 136.3333 | 84 | 69 | 4
21 | 60 | 0 | 21.3333 | 16.9 | 2.17 | 0.086833 | 8.39 | 8.27 | 4.0825 | 136 | 123.6667 | 82 | 67.3333 | 1.3333
22 | 61 | 0 | 21.3333 | 11.9 | 2.5717 | 0.0855 | 8.41 | 8.6117 | 3.7308 | 120 | 130.3333 | 85 | 68.6667 | 0.66667
23 | 50 | 0 | 21.8333 | 14.2 | 2.0017 | 0.0765 | 8.15 | 8.424 | 3.0075 | 130 | 138.6667 | 84 | 80.3333 | 1.6667
24 | 52 | 0 | 21.1667 | 11.8 | 1.98 | 0.0655 | 8.42 | 8.7783 | 4.1542 | 110 | 133.6667 | 80 | 66.6667 | 5
25 | 56 | 1 | 20.6667 | 8.47 | 1.965 | 0.12083 | 8.64 | 8.8983 | 3.6233 | 110 | 131.3333 | 79 | 66 | 3.3333
26 | 40 | 1 | 20.25 | 14.4 | 2.155 | 0.1165 | 8.28 | 8.925 | 4.0275 | 120 | 127 | 80 | 66.5 | 6
27 | 39 | 1 | 18.6667 | 4.13 | 2.3133 | 0.112 | 8.39 | 9.035 | 3.9292 | 110 | 118.6667 | 85 | 62 | 6.6667
28 | 41 | 1 | 17.6667 | 137 | 2.0083 | 0.0965 | 8.41 | 8.8633 | 3.695 | 128 | 125.6667 | 84 | 64 | 3
29 | 37 | 0 | 17.1667 | 16 | 2.65 | 0.1285 | 8.46 | 9.2233 | 3.9142 | 112 | 122 | 84 | 66.6667 | 4.3333
30 | 45 | 0 | 16.6667 | 15.5 | 2.0117 | 0.11567 | 8.41 | 8.755 | 3.9333 | 115 | 135 | 85 | 71.3333 | 0
31 | 55 | 0 | 17.1667 | 14.4 | 2.2383 | 0.24483 | 8.42 | 8.7917 | 3.9525 | 115 | 129 | 90 | 72.6667 | 3.3333
TOTAL |  | 4
AVG. | 59.6452 | 0.12903 | 20.9866 | 14.929 | 2.4352 | 0.095602 | 8.5768 | 8.6824 | 3.8466 | 116.5161 | 130.6989 | 80.6452 | 67.1559 | 2.7957
MAX. | 79 | 1 | 22.8333 | 137 | 3.248 | 0.24483 | 9.12 | 9.2233 | 4.5983 | 140 | 145.3333 | 90 | 80.3333 | 6.6667
MIN. | 37 | 0 | 16.6667 | 4.13 | 1.965 | 0.0655 | 8.15 | 8.27 | 3.0075 | 100 | 118.6667 | 68 | 55.6667 | 0

## Filter
| WATER TREATMENT PLANT MONTHLY FILTER REPORT | [8 empty] | Month, Year: October 2020
Date | FILTER DATA
| NUMBER IN SERVICE | AVG. HOURS IN SERVICE | AVG. HRS. RUN BETWEEN WASH | AVG. MAX. LOSS OF HEAD | WASHWATER (TOTAL ONLY) TG | NO. FILTERS WASHED | gal | lbs | lbs | lbs | lbs | ppm
[7 empty] | LAS | IRON | CL2 | POLY | POT. | IRON | POLY | LAS | CL2 | POT.
1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 1905.7 | 700 | 470.25 | 55 | 41.7 | 10.2892 | 0 | 15.3162 | 1.2034
2 | 4 | 24 | 192 | 0.51 | 126 | 1 | 0 | 2596.92 | 1020 | 1197 | 55 | 40.0748 | 18.4717 | 0 | 15.7403 | 0.84874
3 | 5 | 24 | 134 | 0.49 | 126 | 1 | 0 | 1976.76 | 640 | 453.15 | 55 | 41.0783 | 9.4167 | 0 | 13.2996 | 1.1429
4 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 2454.8 | 800 | 538.65 | 81 | 40.9945 | 8.9953 | 0 | 13.3598 | 1.3527
5 | 5 | 24 | 117 | 4.68 | 109 | 1 | 0 | 2306.22 | 760 | 555.75 | 66 | 41.2724 | 9.9458 | 0 | 13.6011 | 1.1811
6 | 4 | 24 | 109 | 0.96 | 90 | 1 | 0 | 2487.1 | 720 | 598.5 | 73 | 42.0611 | 10.1217 | 0 | 12.1764 | 1.2346
7 | 4 | 24 | 195 | 0.51 | 135 | 1 | 0 | 2506.48 | 760 | 1111.5 | 55 | 41.9159 | 18.5876 | 0 | 12.7095 | 0.91977
8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2261 | 1940 | 1111.5 | 55 | 39.8681 | 19.599 | 0 | 34.2079 | 0.96981
9 | 5 | 24 | 102 | 9.53 | 118 | 1 | 0 | 2370.82 | 820 | 1111.5 | 55 | 35.7124 | 16.7429 | 0 | 12.3519 | 0.82848
10 | 5 | 24 | 177 | 0.48 | 276 | 1 | 0 | 2538.78 | 700 | 598.5 | 55 | 49.0984 | 11.5746 | 0 | 13.5376 | 1.0637
11 | 5 | 24 | 0 | 0 | 0 | 0 | 0 | 2383.74 | 780 | 598.5 | 55 | 42.3437 | 10.6315 | 0 | 13.8556 | 0.977
12 | 5 | 24 | 350 | 0.96 | 177 | 2 | 0 | 2596.92 | 780 | 769.5 | 73 | 41.9087 | 12.4181 | 0 | 12.5875 | 1.1781
13 | 4 | 24 | 118 | 0.02 | 98 | 1 | 0 | 2347.887 | 760 | 769.5 | 60 | 42.2705 | 13.8538 | 0 | 13.6827 | 1.0802
14 | 5 | 24 | 0 | 0 | 0 | 0 | 0 | 2558.16 | 780 | 598.5 | 87 | 40.5197 | 9.4799 | 0 | 12.3547 | 1.378
15 | 4 | 24 | 180 | 0.73 | 113 | 1 | 0 | 2163.8416 | 720 | 769.5 | 85 | 42.3252 | 15.0516 | 0 | 14.0833 | 1.6626
16 | 5 | 24 | 0 | 0 | 0 | 0 | 0 | 2273.92 | 780 | 705.375 | 80 | 42.7355 | 13.2566 | 0 | 14.6591 | 1.5035
17 | 4 | 24 | 113 | 6.48 | 198 | 2 | 0 | 2131.8 | 650 | 470.25 | 55 | 41.9723 | 9.2586 | 0 | 12.7976 | 1.0829
18 | 4 | 24 | 184 | 0.48 | 92 | 1 | 0 | 2118.88 | 590 | 495.9 | 31 | 41.8554 | 9.7958 | 0 | 11.6546 | 0.61236
19 | 5 | 24 | 293 | 1.2 | 200 | 2 | 0 | 2693.82 | 800 | 555.75 | 74 | 41.199 | 8.4996 | 0 | 12.2351 | 1.1317
20 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 2293.3 | 760 | 513 | 5 | 40.6168 | 9.0858 | 0 | 13.4604 | 0.088555
21 | 4 | 24 | 0 | 0 | 0 | 0 | 0 | 2157.64 | 660 | 538.65 | 26 | 41.1303 | 10.2681 | 0 | 12.5813 | 0.49563
22 | 4 | 24 | 99 | 0.5 | 95 | 1 | 0 | 2301.5042 | 720 | 384.75 | 29 | 41.8755 | 7.0005 | 0 | 13.1003 | 0.52765
23 | 4 | 24 | 0 | 0 | 0 | 0 | 47 | 1879.86 | 750 | 427.5 | 55 | 40.5401 | 9.2192 | 1.0136 | 16.1741 | 1.1861
24 | 4 | 24 | 0 | 0 | 0 | 0 | 43 | 1569.78 | 250 | 410.4 | 27 | 37.8718 | 9.9011 | 1.0374 | 6.0314 | 0.65139
25 | 4 | 24 | 212 | 3.9 | 201 | 2 | 51 | 1860.48 | 320 | 427.5 | 28 | 40.1944 | 9.2359 | 1.1018 | 6.9134 | 0.60492
26 | 4 | 24 | 134 | 0.74 | 221 | 2 | 48 | 1692.52 | 360 | 384.75 | 40 | 39.3295 | 8.9405 | 1.1154 | 8.3654 | 0.92949
27 | 4 | 24 | 162 | 0.23 | 118 | 1 | 42 | 1582.7 | 300 | 410.4 | 24 | 37.5044 | 9.725 | 0.99525 | 7.1089 | 0.56871
28 | 4 | 24 | 182 | 1.98 | 119 | 1 | 44 | 1615 | 300 | 427.5 | 46 | 36.7448 | 9.7266 | 1.0011 | 6.8257 | 1.0466
29 | 5 | 20 | 0 | 0 | 0 | 0 | 51 | 2009.06 | 620 | 530.1 | 22 | 38.8539 | 10.2518 | 0.98631 | 11.9904 | 0.42547
30 | 4 | 24 | 113 | 0.48 | 100 | 1 | 53 | 2034.9 | 360 | 495.9 | 33 | 38.1835 | 9.3052 | 0.99451 | 6.7552 | 0.61922
31 | 4 | 24 | 118 | 0.48 | 82 | 1 | 46 | 1679.6 | 300 | 427.5 | 27 | 36.8173 | 9.3709 | 1.0083 | 6.5761 | 0.59185
TOTAL |  | 692 |  |  | 2794 | 25 | 425 | 67349.8928 | 21200 | 18857.025 | 1540
AVG | 4.3871 |  | 105.9355 | 1.14 | 90.129 | 0.80645 | 13.7097 | 2344.3927 | 683.871 | 758.6182 | 51.3333 | 40.4988 | 11.2265 | 0.29851 | 12.5837 | 0.9383
MIN | 4 |  | 0 | 0 | 0 | 0 | 0 | 1905.7 | 250 | 453.15 | 5 | 36.7448 | 7.0005 | 0 | 6.0314 | 0.088555
MAX | 5 |  | 350 | 9.53 | 276 | 2 | 53 | 2596.92 | 1940 | 1197 | 87 | 42.7355 | 19.599 | 1.1154 | 34.2079 | 1.6626

## Monthly Chemical Report
Month, Year: |  | October/1/2020 | Water Treatment Plant Monthly Chemical Report
Month, Year: |  | #NAME?
|  | LAS |  |  | Ferric |  |  | Chlorine (lbs) |  |  | Polymer (lbs) |  |  | KMnO4 (lbs) |  |  | Lime |  |  | PAC |  |  | Potassium (lbs) |  |  | LIME
Date | Raw Water Treated (MGD) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | $ Per Day (treated water) | (lbs) | $ Per MGD (treated water) | Cost Per Day (treated water) | $ Per Day (treated water) | Total $Per MGD | Total $ Per Day
1 | 5.48 | 0 | 0 | 0 | 3811.4 | 65.7258 | 360.1773 | 700 | 45.9215 | 251.65 | 470.25 | 62.6428 | 343.2825 | [9 empty] | 55 | 21.0214 | 115.1975 | 180.84 | 195.3116 | 1251.1473
2 | 7.77 | 0 | 0 | 0 | 5193.84 | 63.1683 | 490.8179 | 1020 | 47.1931 | 366.69 | 1197 | 112.4595 | 873.81 | [9 empty] | 55 | 14.8259 | 115.1975 | 256.41 | 237.6468 | 2102.9254
3 | 5.77 | 0 | 0 | 0 | 3953.52 | 64.75 | 373.6076 | 640 | 39.8752 | 230.08 | 453.15 | 57.3309 | 330.7995 | [9 empty] | 55 | 19.9649 | 115.1975 | 190.41 | 181.9211 | 1240.0946
4 | 7.18 | 0 | 0 | 0 | 4909.6 | 64.618 | 463.9572 | 800 | 40.0557 | 287.6 | 538.65 | 54.7653 | 393.2145 | [9 empty] | 81 | 23.6288 | 169.6545 | 236.94 | 183.0677 | 1551.3662
5 | 6.7 | 0 | 0 | 0 | 4612.44 | 65.0561 | 435.8756 | 760 | 40.7791 | 273.22 | 555.75 | 60.5519 | 405.6975 | [9 empty] | 66 | 20.6324 | 138.237 | 221.1 | 187.0194 | 1474.1301
6 | 7.09 | 0 | 0 | 0 | 4974.2 | 66.2993 | 470.0619 | 720 | 36.5078 | 258.84 | 598.5 | 61.6227 | 436.905 | [9 empty] | 73 | 21.5654 | 152.8985 | 233.97 | 185.9951 | 1552.6754
7 | 7.17 | 0 | 0 | 0 | 5012.96 | 66.0704 | 473.7247 | 760 | 38.106 | 273.22 | 1111.5 | 113.1653 | 811.395 | [9 empty] | 55 | 16.0666 | 115.1975 | 236.61 | 233.4083 | 1910.1472
8 | 6.8 | 0 | 0 | 0 | 4522 | 62.8425 | 427.329 | 1940 | 102.5632 | 697.43 | 1111.5 | 119.3228 | 811.395 | [9 empty] | 55 | 16.9408 | 115.1975 | 224.4 | 301.6693 | 2275.7515
9 | 7.96 | 0 | 0 | 0 | 4741.64 | 56.2921 | 448.085 | 820 | 37.0339 | 294.79 | 1111.5 | 101.934 | 811.395 | [9 empty] | 55 | 14.472 | 115.1975 | 262.68 | 209.7321 | 1932.1475
10 | 6.2 | 0 | 0 | 0 | 5077.56 | 77.3918 | 479.8294 | 700 | 40.5887 | 251.65 | 598.5 | 70.4685 | 436.905 | [9 empty] | 55 | 18.5802 | 115.1975 | 204.6 | 207.0293 | 1488.1819
11 | 6.75 | 0 | 0 | 0 | 4767.48 | 66.7447 | 450.5269 | 780 | 41.5422 | 280.41 | 598.5 | 64.7267 | 436.905 | [9 empty] | 55 | 17.0663 | 115.1975 | 222.75 | 190.0799 | 1505.7894
12 | 7.43 | 0 | 0 | 0 | 5193.84 | 66.0589 | 490.8179 | 780 | 37.7402 | 280.41 | 769.5 | 75.6036 | 561.735 | [9 empty] | 73 | 20.5785 | 152.8985 | 245.19 | 199.9813 | 1731.0514
13 | 6.66 | 0 | 0 | 0 | 4695.774 | 66.6292 | 443.7506 | 760 | 41.024 | 273.22 | 769.5 | 84.3446 | 561.735 | [9 empty] | 60 | 18.8694 | 125.67 | 219.78 | 210.8672 | 1624.1556
14 | 7.57 | 0 | 0 | 0 | 5116.32 | 63.8695 | 483.4922 | 780 | 37.0423 | 280.41 | 598.5 | 57.7153 | 436.905 | [9 empty] | 87 | 24.0715 | 182.2215 | 249.81 | 182.6986 | 1632.8387
15 | 6.13 | 0 | 0 | 0 | 4327.6832 | 66.7155 | 408.9661 | 720 | 42.2251 | 258.84 | 769.5 | 91.637 | 561.735 | [9 empty] | 85 | 29.0428 | 178.0325 | 202.29 | 229.6205 | 1609.8636
16 | 6.38 | 0 | 0 | 0 | 4547.84 | 67.3622 | 429.7709 | 780 | 43.9514 | 280.41 | 705.375 | 80.7091 | 514.9238 | [9 empty] | 80 | 26.2633 | 167.56 | 210.54 | 218.286 | 1603.2046
17 | 6.09 | 0 | 0 | 0 | 4263.6 | 66.1593 | 402.9102 | 650 | 38.3703 | 233.675 | 470.25 | 56.3682 | 343.2825 | [9 empty] | 55 | 18.9158 | 115.1975 | 200.97 | 179.8137 | 1296.0352
18 | 6.07 | 0 | 0 | 0 | 4237.76 | 65.975 | 400.4683 | 590 | 34.9432 | 212.105 | 495.9 | 59.6387 | 362.007 | [9 empty] | 31 | 10.6968 | 64.9295 | 200.31 | 171.2537 | 1239.8198
19 | 7.84 | 0 | 0 | 0 | 5387.64 | 64.9403 | 509.132 | 800 | 36.6837 | 287.6 | 555.75 | 51.7471 | 405.6975 | [9 empty] | 74 | 19.7695 | 154.993 | 258.72 | 173.1406 | 1616.1425
20 | 6.77 | 0 | 0 | 0 | 4586.6 | 64.0227 | 433.4337 | 760 | 40.3575 | 273.22 | 513 | 55.3161 | 374.49 | [9 empty] | 5 | 1.5469 | 10.4725 | 223.41 | 161.2432 | 1315.0262
21 | 6.29 | 0 | 0 | 0 | 4315.28 | 64.8321 | 407.794 | 660 | 37.7218 | 237.27 | 538.65 | 62.5142 | 393.2145 | [9 empty] | 26 | 8.6577 | 54.457 | 207.57 | 173.7258 | 1300.3055
22 | 6.59 | 0 | 0 | 0 | 4603.0084 | 66.0067 | 434.9843 | 720 | 39.2777 | 258.84 | 384.75 | 42.6203 | 280.8675 | [9 empty] | 29 | 9.2171 | 60.7405 | 217.47 | 157.1217 | 1252.9023
23 | 5.56 | 480.81 | 9.253 | 51.4467 | 3759.72 | 63.9017 | 355.2935 | 750 | 48.4937 | 269.625 | 427.5 | 56.1286 | 312.075 | [9 empty] | 55 | 20.719 | 115.1975 | 183.48 | 198.496 | 1287.1177
24 | 4.97 | 439.89 | 9.4705 | 47.0682 | 3139.56 | 59.6959 | 296.6884 | 250 | 18.0835 | 89.875 | 410.4 | 60.2801 | 299.592 | [9 empty] | 27 | 11.3786 | 56.5515 | 164.01 | 158.9085 | 953.7852
25 | 5.55 | 521.73 | 10.0586 | 55.8251 | 3720.96 | 63.3569 | 351.6307 | 320 | 20.7279 | 115.04 | 427.5 | 56.2297 | 312.075 | [9 empty] | 28 | 10.5668 | 58.646 | 183.15 | 160.94 | 1076.3668
26 | 5.16 | 491.04 | 10.1824 | 52.5413 | 3385.04 | 61.9935 | 319.8863 | 360 | 25.0814 | 129.42 | 384.75 | 54.4317 | 280.8675 | [9 empty] | 40 | 16.2364 | 83.78 | 170.28 | 167.9254 | 1036.7751
27 | 5.06 | 429.66 | 9.0857 | 45.9736 | 3165.4 | 59.1167 | 299.1303 | 300 | 21.3142 | 107.85 | 410.4 | 59.2079 | 299.592 | [9 empty] | 24 | 9.9344 | 50.268 | 166.98 | 158.6589 | 969.7939
28 | 5.27 | 450.12 | 9.1391 | 48.1628 | 3230 | 57.9194 | 305.235 | 300 | 20.4649 | 107.85 | 427.5 | 59.2173 | 312.075 | [9 empty] | 46 | 18.2822 | 96.347 | 173.91 | 165.0227 | 1043.5798
29 | 6.2 | 521.73 | 9.004 | 55.8251 | 4018.12 | 61.2439 | 379.7123 | 620 | 35.95 | 222.89 | 530.1 | 62.415 | 386.973 | [9 empty] | 22 | 7.4321 | 46.079 | 204.6 | 176.0451 | 1296.0795
30 | 6.39 | 542.19 | 9.0789 | 58.0143 | 4069.8 | 60.1872 | 384.5961 | 360 | 20.2535 | 129.42 | 495.9 | 56.6521 | 362.007 | [9 empty] | 33 | 10.8167 | 69.1185 | 210.87 | 156.9884 | 1214.0259
31 | 5.47 | 470.58 | 9.2051 | 50.3521 | 3359.2 | 58.0337 | 317.4444 | 300 | 19.7166 | 107.85 | 427.5 | 57.0521 | 312.075 | [9 empty] | 27 | 10.3385 | 56.5515 | 180.51 | 154.3461 | 1024.783
Total | 198.32 |  |  | 465.2092 |  |  | 12729.1297 |  |  | 7621.4 |  |  | 13765.6282 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 3282.0815 | 6544.56 | 5867.964 | 44408.0087
Avg. | 6.3974 | 140.25 | 2.7251 | 15.0068 | 4345.1544 | 64.0961 | 410.6171 | 683.871 | 37.7287 | 245.8516 | 608.2911 | 68.349 | 444.0525 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 50.5484 | 16.3903 | 105.8736 | 211.1148 | 223.921 | 1432.5164
Max | 7.96 | 542.19 | 10.1824 | 58.0143 | 5387.64 | 77.3918 | 509.132 | 1940 | 102.5632 | 697.43 | 1197 | 119.3228 | 873.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 29.0428 | 182.2215 | 262.68 | 301.6693 | 2275.7515
Min. | 4.97 | 0 | 0 | 0 | 3139.56 | 56.2921 | 296.6884 | 250 | 18.0835 | 89.875 | 384.75 | 42.6203 | 280.8675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1.5469 | 10.4725 | 164.01 | 154.3461 | 953.7852
|  | Ammonia $/lb |  | 0.107 | Ferric $/lb |  | 0.0945 | Chlorine $/lb |  | 0.3595 | Polymer $/lb |  | 0.73 | KMnO4 $/lb |  | 0.25 | Lime $/lb |  | 0.25 | PAC $/lb |  | 0.25 | Potassium $/lb |  | 2.0945 | Lime | 33 | Per MGD
|  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract through |  |  | Contract |  | 0.22392 | PerKG

## LAS Meter
Month:
LAS Carrier Water Meter
Prev.
1 | 0 | 0
2 | 0 | 0
3 | 6356060 | 6356060
4 | 6356060 | 0
5 | 6356060 | 0
6 | 6356060 | 0
7 | 6356060 | 0
8 | 6356060 | 0
9 | 6356060 | 0
10 | 6356060 | 0
11 | 6356060 | 0
12 | 0 | -6356060
13 | 6356060 | 6356060
14 | 0 | -6356060
15 | 6356060 | 6356060
16 | 6356060 | 0
17 | 6356060 | 6356060
18 | 6356060 | 0
19 | 6356060 | 0
20 | 6356060 | 0
21 | 6356060 | 0
22 | 6356060 | 0
23 | 0 | -6356060
24 | 6424340 | 6424340
25 | 6463990 | 39650
26 | 6503570 | 39580
27 | 0 | -6503570
28 | 6582850 | 6582850
29 | 6617500 | 34650
30 | 665790 | -5951710
31 | 6697670 | 6031880
Total |  | 13053730

## Graphs
Chemicals | Amount
LAS | 2021.7447
Fe | 12729.1297
CL2 | 7621.4
Poly | 13765.6282
Potassium | 3282.0815
Lime | 0
Chemfloc 3315 | 44408.0087